## OHT
Providing water supply fecilities to Electronic Hardware Manufactering Cluster At Maheshwaram (V&M) R R Dist
Centring Details for 500KL OHT Roof Slab Centering Details
S.no | Description | Nos | L | B | Qty(m2) | Remarks
Roof Slab Centering
1 | Dome Centering(R=(h^2+r^2)/2h)),2*3.147*R*h | 2*3.14 | 8.758 | 1.4 | 77.0007 | 8.758
2 | Flat slab centering | 1*3.14 | 12.1 | 2 | 75.988
7 | Inside Beam Centering (Outside) | 1*3.14 | 10 | 0.9 | 28.26
10 | Balcony Centering for Sides | 1*3.14 | 14.5 | 0.12 | 5.4636
[5 empty] | 186.7123 | Sqm
Steel Details for 500KL OHT Bottom Slab Steel
S.no | Description | Dia of Rod(mm) | Cutting Length | No's | Total No of Rods | Total Length | Weight per Meter | Total Weight | Remarks
A | Inner Ring Beam Steel Details
| Top & Bottom Main Bars | 16mm | 30.772 | 2x4 | 8 | 246.18 | 1.58 | 388.96
| Top Extra Bars | 16mm | 2.5 | 2x6 | 12 | 30 | 1.58 | 47.4
| Bottom Extra Bars | 12mm | 3.5 | 2x6 | 12 | 42 | 0.888 | 37.3
| Outside Face Reinforcement | 12mm | 31.4 | 1x3 | 3 | 94.2 | 0.888 | 83.65
| Inside Face Reinforcement | 12mm | 30.144 | 1x3 | 3 | 90.43 | 0.888 | 80.3
| Inner Rings | 8mm | 1.3 | 1*180 | 180 | 234 | 0.395 | 92.43
B | Flat Slab Steel Details
| Bottom mat Main Bars | 8mm | 3 | 1x254 | 252 | 756 | 0.395 | 298.62
| Bottom mat Cercumferencial Bars | 8mm | 37.994 | 1x14 | 12 | 455.93 | 0.395 | 180.09
| Top mat main Bars | 8mm | 3 | 1x254 | 252 | 756 | 0.395 | 298.62
| Top mat Cercumferential Bars | 8mm | 37.994 | 1x14 | 12 | 455.93 | 0.395 | 180.09
C | Dome Steel Details
| Dome Bottom mat Main Bars | 8mm | 5.3 | 1X102 | 102 | 540.6 | 0.395 | 213.54
| Dome Bottom mat Main Bars | 8mm | 3.5 | 1X102 | 102 | 357 | 0.395 | 141.02
| Dome Bottom Cercumferential Bars | 8mm | 15.7 | 1X33 | 33 | 518.1 | 0.395 | 204.65
| Dome Top mat main Bars | 8mm | 1.9 | 1X240 | 240 | 456 | 0.395 | 180.12
| Dome Top mat Cercumferential Bars | 8mm | 26.69 | 1X10 | 10 | 266.9 | 0.395 | 105.43
| Flat Slab Railing | 10mm | 1.5 | 2X50 | 100 | 150 | 0.617 | 92.55
| Dome Railing | 10mm | 1.5 | 1x12 | 12 | 18 | 0.617 | 11.11
Stair Case Steel
Beam(B2)
| Beam (B1) Main Bars | 12mm | 5.23 | 2x4 | 8 | 41.84 | 0.88889 | 37.19
| Beam (B1) Top Extra Bars | 16mm | 2.465 | 2x2 | 4 | 9.86 | 1.5802 | 15.58
| Beam (B1) Top Extra Bars | 16mm | 1.645 | 2x2 | 4 | 6.58 | 1.5802 | 10.4
| Beam (B1) Bottom Extra Bars | 16mm | 2.95 | 1x2 | 2 | 5.9 | 1.5802 | 9.32
| Stirrups | 8mm | 1.3 | 1x66 | 66 | 85.8 | 0.395 | 33.89
| Beam (B2) Main Bars | 12mm | 3.66 | 2x2 | 4 | 14.64 | 0.88889 | 13.01
| Beam (B2) Top Extra Bars | 16mm | 1.275 | 1x2 | 2 | 2.55 | 1.5802 | 4.03
| Beam (B2) Bottom Extra Bars | 16mm | 2.3 | 1x1 | 1 | 2.3 | 1.5802 | 3.63
| Stirrups | 8mm | 1.3 | 1x18 | 18 | 23.4 | 0.395 | 9.24
Landing Steel
| Landing Bottom Distribution Bars | 10mm | 1.25 | 1x45 | 45 | 56.25 | 0.61728 | 34.72
| Landing Bottom Platform Distribution bars (Balcony) | 10mm | 7 | 1x10 | 10 | 70 | 0.61728 | 43.21 |  |  |  | 0
| Landing top mat Distribution bars | 10mm | 1.25 | 1x15 | 15 | 18.75 | 0.61728 | 11.57
| Landing top mat Main bars | 16mm | 2.55 | 1x13 | 13 | 33.15 | 1.5802 | 52.39
| Landing top mat Distribution bars | 10mm | 1.25 | 1x15 | 15 | 18.75 | 0.61728 | 11.57
| Landing top mat Distribution bars Balcony | 10mm | 7 | 1x10 | 10 | 70 | 0.61728 | 43.21
| Flat slab top main bars | 10mm | 1.25 | 1x40 | 40 | 50 | 0.61728 | 30.86
| Flat slab Bottom main bars | 10mm | 1.25 | 1x40 | 40 | 50 | 0.61728 | 30.86
| Beam Top and Bottom Main Bars (B2) | 12mm | 3.5 | 2x2 | 4 | 14 | 0.888 | 12.43
| Top Extra Bars | 16mm | 1.295 | 1x2 | 2 | 2.59 | 1.58 | 4.09
| Bottom Extra Bars | 16mm | 2.3 | 1x1 | 1 | 2.3 | 1.58 | 3.63
| Stirrups | 8mm | 1.3 | 1x18 | 18 | 23.4 | 0.395 | 9.24
| Railing | 10mm | 1.3 | 1x15 | 15 | 19.5 | 0.617 | 12.03
3071.98
Concrete Details for 500KL ELSR Roof Slab
S.no | Description | Nos | L | B | D | Qty(m3) | Remarks
BOTTOM SLAB CONCRETE
| Inner Ring Beam | 1*3.14 | 9.8 | 0.3 | 0.42 | 1.2348
| Column Between Slab | 1*3.14 | 12.2 | 2.2 | 0.12 | 10.1133
| Dome Concrete |  | 77 | 0.125 |  | 9.625
20.9731
Impervious Coat Details for 500KL ELSR 15mtrs Staging
S.no | Description | Nos |  |  | L | B | Qty(m2) | Remarks
1 | Dome Impervious coat (R=(h^2+r^2)/2h)),2*3.147*R*h | 2 | x | 3.14 | 8.758 | 1.4 | 77.0003
2 | In Between Column Slab Plastering | 1 | x | 3.14 | 12 | 2.2 | 82.896
3 | Bottom Balcony Plastering | 1 | x | 3.14 | 15.4 | 0.9 | 43.5204
4 | Sidewall Outside Plastering | 1 | x | 3.14 | 14.5 | 4.55 | 207.1615
5 | Sidewall Inside Plastering | 1 | x | 3.14 | 14 | 4.43 | 194.7428
6 | Roof Flat Slab plastering | 1 | x | 3.14 | 12 | 2.5 | 94.2
7 | Roof Dome Plastering | 2 | x | 3.14 | 8.758 | 1.4 | 77.0003
[5 empty] | Total Qty (Sqm) |  | 776.5214
500KL ELSR and Staircase and Sump SS Railing Details
S.No | Description | No's |  |  | L | Total Rmt | Remarks
500KL ELSR Railing Details
1 | Bottom Slab Railing | 1 | X | 3.14 | 16 | 50.24
2 | Roof Slab Railing | 1 | X | 3.14 | 14.3 | 44.9
Staircase Railing Details
1 | Landing Railing | 2 | X | 9 | 4.5 | 81
2 | Flat Slab Railing | 1 | X | 9 | 5.16 | 46.44
500KL Sump Railing Details
1 | Sump Roof Slab Railing Details | 1 | X | 3.14 | 13.8 | 43.332
[6 empty] | 265.912 | Rmt
Painting Details for 500KL ELSR 15mtrs Staging
S.no | Description | Nos |  |  |  |  | L | B | Qty(m2) | Remarks
1 | Columns | 1 | x | 12 | x | 4 | 0.5 | 15 | 360
2 | Outer GL Brace (GL+1+2+3) | 6 | x | 4 | x | 2 | 0.3 | 6.5 | 93.6
|  | 6 | x | 4 | x | 2 | 0.6 | 6.5 | 187.2
3 | Inner Brace (GL+1+2+3) | 6 | x | 4 | x | 2 | 0.3 | 4.5 | 64.8
|  | 6 | x | 4 | x | 2 | 0.6 | 4.5 | 129.6
4 | Connecting Beam (GL+1+2+3) | 6 | x | 4 | x | 2 | 0.3 | 1.5 | 21.6
|  | 6 | x | 4 | x | 2 | 0.6 | 1.5 | 43.2
5 | Outer Beam Painting (Outside) | 1 | x | 1 | x | 3.14 | 14 | 1.78 | 78.2488
6 | Inside Beam Painting (Inside) | 1 | x | 1 | x | 3.14 | 10 | 1.79 | 56.206 | x
7 | Dome Centering(R=(h^2+r^2)/2h)),2*3.147*R*h | 1 | x | 2 | x | 3.14 | 8.758 | 1.4 | 77.0007 | 8.758
8 | In Between Column Slab Centering | 1 | x | 1 | x | 3.14 | 12 | 1.5 | 56.52
9 | Bottom Balcony Centering | 1 | x | 1 | x | 3.14 | 15.4 | 0.9 | 43.5204
10 | Sidewall Inside Painting | 1 | x | 1 | x | 1 | 43.96 | 4.43 | 194.7428
11 | Topside Dome Painting(R=(h^2+r^2)/2h)),2*3.147*R*h | 1 | x | 2 | x | 3.14 | 8.758 | 1.4 | 77.0007 | 8.758
12 | Topside In Between Column Slab Painting | 1 | x | 1 | x | 3.14 | 12 | 2.2 | 82.896
13 | Inner Column Painting | 1 | x | 6 | x | 4 | 0.3 | 4.43 | 31.896
14 | Balcony Painting for Sides | 1 | x | 1 | x | 3.14 | 16.3 | 0.12 | 6.1418
15 | Topside Bottom Balcony Painting | 1 | x | 1 | x | 3.14 | 15.4 | 0.9 | 43.5204
16 | Sidewall Outside Painting | 1 | x | 1 | x | 1 | 45.53 | 4.55 | 207.1615
17 | Inside Roof Slab Beam Painting | 1 | x | 1 | x | 3.14 | 10 | 0.9 | 28.26
18 | Inside Roof Flat Slab painting | 1 | x | 1 | x | 1 | 37.68 | 2.5 | 94.2
19 | Inside Roof Dome Painting | 1 | x | 1 | x | 1 | 77 | 1 | 77
20 | Top Side Roof Flat Slab Painting | 1 | x | 1 | x | 1 | 37.68 | 2.5 | 94.2
21 | Top Side Roof Dome Painting | 1 | x | 1 | x | 1 | 77 | 1 | 77
[7 empty] | Total Qty |  | 2225.515
2657.6385
Painting Details for Dogg-Legged Staircase
S.no | Description | Nos |  |  |  |  | L | B | Qty(m2) | Remarks
1 | GL Beam Painting | 1 | x | 2 | x | 2 | 4.355 | 0.23 | 4.0066
|  | 1 | x | 2 | x | 2 | 4.355 | 0.45 | 7.839
|  | 1 | x | 2 | x | 2 | 3.16 | 0.23 | 2.9072
|  | 1 | x | 2 | x | 2 | 3.16 | 0.45 | 5.688
2 | Columns Painting | 1 | x | 4 | x | 2 | 20 | 0.3 | 48
|  | 1 | x | 4 | x | 2 | 20 | 0.45 | 72
3 | 1st Landing
4 | 1st Landing Painting | 1 | x | 1 | x | 1 | 4.35 | 1.3 | 5.655
5 | 1st Landing Sides Painting | 1 | x | 1 | x | 2 | 4.35 | 0.225 | 1.9575
6 | 1st Landing Top Painting | 1 | x | 1 | x | 13 | 1.3 | 0.3 | 5.07
|  | 1 | x | 1 | x | 13 | 1.3 | 0.15 | 2.535
7 | Beam (B2) Painting | 1 | x | 1 | x | 1 | 2.56 | 0.83 | 2.1248
8 | Beam (B1) Painting | 1 | x | 2 | x | 2 | 0.9 | 0.83 | 2.988
9 | 1st Landing Bottom Flat Slab Painting | 1 | x | 1 | x | 1 | 3.16 | 0.9 | 2.844
10 | 1st Landing Sides Flat Slab Painting | 1 | x | 1 | x | 1 | 5.16 | 0.15 | 0.774
11 | 1st Landing Top Flat Slab Painting | 1 | x | 1 | x | 1 | 3.16 | 1 | 3.16
12 | 2nd Landing
13 | Beam(B2) Painting | 1 | x | 1 | x | 2 | 5.125 | 1.36 | 13.94
14 | Beam(B1) Painting | 1 | x | 1 | x | 1 | 2.56 | 0.83 | 2.1248
15 | 2nd Landing Painting | 1 | x | 1 | x | 1 | 4.35 | 1.3 | 5.655
16 | 2nd Landing Sides Painting | 1 | x | 1 | x | 2 | 4.35 | 0.225 | 1.9575
17 | 2nd Landing Top Painting | 1 | x | 1 | x | 13 | 1.3 | 0.3 | 5.07
|  | 1 | x | 1 | x | 13 | 1.3 | 0.15 | 2.535
18 | 2st Landing Bottom Flat Slab Painting | 1 | x | 1 | x | 1 | 3.16 | 0.9 | 2.844
19 | 2st Landing Sides Flat Slab Painting | 1 | x | 1 | x | 1 | 5.16 | 0.15 | 0.774
20 | 2st Landing Top Flat Slab Painting | 1 | x | 1 | x | 1 | 3.16 | 1 | 3.16
21 | 3rd Landing
22 | 3rd Landing Painting | 1 | x | 1 | x | 1 | 4.35 | 1.3 | 5.655
23 | 3rd Landing Sides Painting | 1 | x | 1 | x | 2 | 4.35 | 0.225 | 1.9575
24 | 3rd Landing Top Painting | 1 | x | 1 | x | 13 | 1.3 | 0.3 | 5.07
|  | 1 | x | 1 | x | 13 | 1.3 | 0.15 | 2.535
25 | Beam (B2) Painting | 1 | x | 1 | x | 1 | 2.56 | 0.83 | 2.1248
26 | Beam (B1) Painting | 1 | x | 2 | x | 2 | 0.9 | 0.83 | 2.988
27 | 3rd Landing Bottom Flat Slab Painting | 1 | x | 1 | x | 1 | 3.16 | 0.9 | 2.844
28 | 3rd Landing Sides Flat Slab Painting | 1 | x | 1 | x | 1 | 5.16 | 0.15 | 0.774
29 | 3rd Landing Top Flat Slab Painting | 1 | x | 1 | x | 1 | 3.16 | 1 | 3.16
30 | 4th Landing
31 | Beam(B2) Painting | 1 | x | 1 | x | 2 | 5.125 | 1.36 | 13.94
32 | Beam(B1) Painting | 1 | x | 1 | x | 1 | 2.56 | 0.83 | 2.1248
33 | 4th Landing Painting | 1 | x | 1 | x | 1 | 4.35 | 1.3 | 5.655
34 | 4th Landing Sides Painting | 1 | x | 1 | x | 2 | 4.35 | 0.225 | 1.9575
35 | 4th Landing Top Painting | 1 | x | 1 | x | 13 | 1.3 | 0.3 | 5.07
|  | 1 | x | 1 | x | 13 | 1.3 | 0.15 | 2.535
36 | 4th Landing Bottom Flat Slab Painting | 1 | x | 1 | x | 1 | 3.16 | 0.9 | 2.844
37 | 4th Landing Sides Flat Slab Painting | 1 | x | 1 | x | 1 | 5.16 | 0.15 | 0.774
38 | 4th Landing Top Flat Slab Painting | 1 | x | 1 | x | 1 | 3.16 | 1 | 3.16
39 | 5th Landing
40 | 5th Landing Painting | 1 | x | 1 | x | 1 | 4.35 | 1.3 | 5.655
41 | 5th Landing Sides Painting | 1 | x | 1 | x | 2 | 4.35 | 0.225 | 1.9575
42 | 5th Landing Top Painting | 1 | x | 1 | x | 13 | 1.3 | 0.3 | 5.07
|  | 1 | x | 1 | x | 13 | 1.3 | 0.15 | 2.535
43 | Beam (B2) Painting | 1 | x | 1 | x | 1 | 2.56 | 0.83 | 2.1248
44 | Beam (B1) Painting | 1 | x | 2 | x | 2 | 0.9 | 0.83 | 2.988
45 | 5th Landing Bottom Flat Slab Painting | 1 | x | 1 | x | 1 | 3.16 | 0.9 | 2.844
46 | 5th Landing Sides Flat Slab Painting | 1 | x | 1 | x | 1 | 5.16 | 0.15 | 0.774
47 | 5th Landing Top Flat Slab Painting | 1 | x | 1 | x | 1 | 3.16 | 1 | 3.16
48 | 6th Landing
49 | Beam(B2) Painting | 1 | x | 1 | x | 2 | 5.125 | 1.36 | 13.94
50 | Beam(B1) Painting | 1 | x | 1 | x | 1 | 2.56 | 0.83 | 2.1248
51 | 6th Landing Painting | 1 | x | 1 | x | 1 | 4.35 | 1.3 | 5.655
52 | 6th Landing Sides Painting | 1 | x | 1 | x | 2 | 4.35 | 0.225 | 1.9575
53 | 6th Landing Top Painting | 1 | x | 1 | x | 13 | 1.3 | 0.3 | 5.07
|  | 1 | x | 1 | x | 13 | 1.3 | 0.15 | 2.535
54 | 6th Landing Bottom Flat Slab Painting | 1 | x | 1 | x | 1 | 3.16 | 0.9 | 2.844
55 | 6th Landing Sides Flat Slab Painting | 1 | x | 1 | x | 1 | 5.16 | 0.15 | 0.774
56 | 6th Landing Top Flat Slab Painting | 1 | x | 1 | x | 1 | 3.16 | 1 | 3.16
57 | 7th Landing
58 | 7th Landing Painting | 1 | x | 1 | x | 1 | 4.35 | 1.3 | 5.655
59 | 7th Landing Sides Painting | 1 | x | 1 | x | 2 | 4.35 | 0.225 | 1.9575
60 | 7th Landing Top Painting | 1 | x | 1 | x | 13 | 1.3 | 0.3 | 5.07
|  | 1 | x | 1 | x | 13 | 1.3 | 0.15 | 2.535
61 | Beam (B2) Painting | 1 | x | 1 | x | 1 | 2.56 | 0.83 | 2.1248
62 | Beam (B1) Painting | 1 | x | 2 | x | 2 | 0.9 | 0.83 | 2.988
63 | 7th Landing Bottom Flat Slab Painting | 1 | x | 1 | x | 1 | 3.16 | 0.9 | 2.844
64 | 7th Landing Sides Flat Slab Painting | 1 | x | 1 | x | 1 | 5.16 | 0.15 | 0.774
65 | 7th Landing Top Flat Slab Painting | 1 | x | 1 | x | 1 | 3.16 | 1 | 3.16
66 | Bottom Slab Connecting Slab | 1 | x | 1 | x | 1 | 1 | 1.3 | 1.3
67 | 8th Landing
68 | Beam(B2) Painting | 1 | x | 1 | x | 2 | 5.125 | 1.36 | 13.94
69 | Beam(B1) Painting | 1 | x | 1 | x | 1 | 2.56 | 0.83 | 2.1248
70 | 8th Landing Painting | 1 | x | 1 | x | 1 | 4.35 | 1.3 | 5.655
71 | 8th Landing Sides Painting | 1 | x | 1 | x | 2 | 4.35 | 0.225 | 1.9575
72 | 8th Landing Top Painting | 1 | x | 1 | x | 13 | 1.3 | 0.3 | 5.07
|  | 1 | x | 1 | x | 13 | 1.3 | 0.15 | 2.535
73 | 8th Landing Bottom Flat Slab Painting | 1 | x | 1 | x | 1 | 3.16 | 0.9 | 2.844
74 | 8th Landing Sides Flat Slab Painting | 1 | x | 1 | x | 1 | 5.16 | 0.15 | 0.774
75 | 8th Landing Top Flat Slab Painting | 1 | x | 1 | x | 1 | 3.16 | 1 | 3.16
76 | 9th Landing
77 | 9th Landing Painting | 1 | x | 1 | x | 1 | 4.35 | 1.3 | 5.655
78 | 9th Landing Sides Painting | 1 | x | 1 | x | 2 | 4.35 | 0.225 | 1.9575
79 | 9th Landing Top Painting | 1 | x | 1 | x | 13 | 1.3 | 0.3 | 5.07
|  | 1 | x | 1 | x | 13 | 1.3 | 0.15 | 2.535
80 | Beam (B2) Painting | 1 | x | 1 | x | 1 | 2.56 | 0.83 | 2.1248
81 | Beam (B1) Painting | 1 | x | 2 | x | 2 | 0.9 | 0.83 | 2.988
82 | 9th Landing Bottom Flat Slab Painting | 1 | x | 1 | x | 1 | 3.16 | 0.9 | 2.844
83 | 9th Landing Sides Flat Slab Painting | 1 | x | 1 | x | 1 | 5.16 | 0.15 | 0.774
84 | 9th Landing Top Flat Slab Painting | 1 | x | 1 | x | 1 | 3.16 | 1 | 3.16
85 | Roof Slab Connecting Slab | 1 | x | 1 | x | 1 | 2 | 1.3 | 2.6
[6 empty] | Total Qty (Sqm) |  |  | 432.1235
Supplimentary Item
1 | Supply and delivery of DI D/F Gate Valves (Soft Seated) Resilient seated soft, sealing gate valves (Sluice valves) with body bonnet of ductile cast iron of grade GGG-40/ SG-400/15 or GGG-50/SG-500/7 or equivalent grade as per I.S.3896-part2-1985 and subsequent revisions, wedge fully rubber lined with EPDM food grade quality and seals of NBR and the valves should be of vacuum tight and 100% leak proof with face to face dimensions as per BS5163-89/IS14846-2000/DIN 3202 F 4. All the valves should be with Electrostatic powder coating both inside and outside pocket less body passage. Drilled as per requirement of the department including cost and conveyance of material to work site, as directed by Engineer-in-Charge for finished item of work, except GST.
i | A)80mm Dia Scour valve for Pipeline |  |  |  | 1No | 2 |  |  | 2
ii | B)150mm Dia Gate valve for OHT Scour |  |  |  | 1No | 1 |  |  | 1
iii | C)400mm Dia Gate valve for Sump Scour |  |  |  | 1No | 1 |  |  | 1
2 | Lowering, keeping in position and fixing C.I. sluice valves (with cap / with hand wheel & reflex valves) excluding cost of bolts, nuts, rubber insertion, sluice valve and tail pieces,as directed by Engineer-in-Charge etc., complete for finished item of work, except GST.
i | A)80mm Dia Scour valve for Pipeline |  |  |  | 1No | 2 |  |  | 2
ii | B)150mm Dia Gate valve for OHT Scour |  |  |  | 1No | 1 |  |  | 1
iii | C)400mm Dia Gate valve for Sump Scour |  |  |  | 1No | 1 |  |  | 1
3 | Jointing CI pipes, fittings and valves with flanged ends including cost of jointing materials such as bolts, rubber insertion, white lead including filling with water, with lead up to 500 meters and testing to required pressure complete. (Reference to specifications. BIS No.3114/1994.), as directed by Engineer-in-Charge for finished item of wor, except GST.
i | A)80mm Dia Scour valve for Pipeline |  |  |  | 1No | 2 |  |  | 2
ii | B)150mm Dia Gate valve for OHT Scour |  |  |  | 1No | 1 |  |  | 1
iii | C)400mm Dia Gate valve for Sump Scour |  |  |  | 1No | 1 |  |  | 1
4 | Centrifugally cast (spun) Ductile Iron pressure pies with flanged (welded) ends for water,gas,sewage conforming to IS: 8329/2000 in standard working lengths of 1,2,3,4,5 mts for classification K9 with cement mortar lining inside the pipes with outside zone coating Rates are ex-factory,excluding transportation & taxes
A | For 500KL ELSR
i | A)250mm DIA D/F Flanged Pipes (1Mtr Length) For Inlet |  |  |  | 1No | 4 |  |  | 4
ii | B)250mm DIA D/F Flanged Pipes (2Mtr Length) For Inlet |  |  |  | 1No | 9 |  |  | 9
i | C)250mm DIA D/F Flanged Pipes (1Mtr Length) For Outlet |  |  |  | 1No | 4 |  |  | 4
ii | D)250mm DIA D/F Flanged Pipes (2Mtr Length) For Outlet |  |  |  | 1No | 9 |  |  | 9
i | E)250mm DIA D/F Flanged Pipes (1Mtr Length) For Over flow |  |  |  | 1No | 5 |  |  | 5
ii | F)250mm DIA D/F Flanged Pipes (2Mtr Length) For Over Flow |  |  |  | 1No | 9 |  |  | 9
iv | G)150mm DIA D/F Flanged Pipes (1Mtr Length) For Scour |  |  |  | 1No | 5 |  |  | 5
v | H)150mm DIA D/F Flanged Pipes (2Mtr Length) For Scour |  |  |  | 1No | 8 |  |  | 8
B | For 500KL Sump
i | A)250mm DIA D/F Flanged Pipes (1Mtr Length) For Inlet |  |  |  | 1No | 4 |  |  | 4
ii | B)250mm DIA D/F Flanged Pipes (2Mtr Length) For Inlet |  |  |  | 1No | 3 |  |  | 3
ii | C)250mm DIA D/F Flanged Pipes (2Mtr Length) For Outlet |  |  |  | 1No | 2 |  |  | 2
iii | D)250mm DIA D/F Flanged Pipes (4Mtr Length) For Outlet |  |  |  | 1No | 4 |  |  | 4
5 | Centrifugally cast (span) Ductile Iron Fittings conforming to IS:9523/2000 having dimensions as per table. The rates mentioned here under are for fitting,zinc coated externally with inside mortor lining (with finishing as per class 13/IS 9523/2000) (ex-works) Excluding Tranportation and Taxes
i | For 500KL ELSR Requirement
a)Duct-foot Bend
| 150mm | 1x1 |  | 27kg/1No |  | 27 | Kgs
| 250mm | 1x3 | @ | 69kg/1No |  | 210 | Kgs
b)Flanged spigot
| 250mm | 1x4 | @ | 32kg/1No |  | 128 | Kgs
c)Flanged Socket
| 250mm | 1x3 | @ | 28kg/1No |  | 84 | Kgs
c)Bell-mouth
| 250mm | 1x1 | @ | 20kg/1No |  | 21 | Kgs
b)90 Degree bend
| 250mm | 1*1 | @ | 50kgs/1No |  | 50 | Kgs
[6 empty] | 520 | Kgs
ii | For 500KL Sump Requirement
a)Duct-foot Bend
| 250mm | 1x1 | @ | 69kg/1No |  | 69 | Kgs
b)90 Degree bend
| 250mm | 1*4 | @ | 50kgs/1No |  | 200 | Kgs
| 400mm (Scour) | 1*1 | @ | 128kgs/No |  | 128 | Kgs
c)Bell-mouth
| 250mm | 1x1 | @ | 20kg/1No |  | 20 | Kgs
d)Flanged Spigot
| 400mm (Scour) | 1x1 | @ | 70kg/1No |  | 70 | Kgs
[6 empty] | 487 | Kgs
6 | Providing and laying of Vibrated Reinforced Cement Concrete corresponding to M-30 grade Design Mix Concrete corresponding to IS 456 using weigh batcher with 20mm size well graded machine crushed hard granite chips (Coarse aggregate) from approved quarry with a minimum cement content of 400 kg/CuM including cost and conveyance of all materials like cement, Coarse aggregate, Fine aggregate, water etc., to site, including centering & shuttering using steel scaffolding pipes, jack props, wallers, foot plates, brackets, steel centering plates weigh batcher etc machine mixing, laying concrete, vibrating, finishing smooth to required levels, curing, pumping to work spot, lifting of material with mechanical equipment like winch, etc., all other incidental and operational charges, all labour charges, etc., but excluding cost of steel and its fabrication charges etc., complete as directed by Engineer-in-Charge for the following finished items of work, excluding GST & seigniorage charges.
i | RCC SLAB For Sluice Valve Chambers for ELSR |  |  |  | 1Cum | 1 |  |  | 1
ii | RCC SLAB For Sluice Valve Chambers for Sump |  |  |  | 1Cum | 1 |  |  | 1
iii | Pedestals Concrete |  |  |  | 1Cum | 3 |  |  | 3
7 | Supply and Fixing water level indicater containing indicater with suitable probe height with chain pully arrengement and using 15m standard cable as per site reserviour with 250mm dia ball and 40mm squre pipe frame conforming to IS 1230 Drilling hole in roof slab including all accessories etc., complete as directed by the department officers, excluding GST
i | For 500KL ELSR |  |  |  | 1 JOB | 1
ii | For 500KL GLSR |  |  |  | 1 JOB | 1
8 | Manifacturing,supply,delivery and fixing at site, the lightening protective system with copper plates and connecters with protective coating,including suitable earthing arrengements as per the standard specifications including cost and conveyance, labour charges etc.,complete as directed by the departmental officers, except GST
i | For 500KL ELSR |  |  |  | 1No | 1
ii | For 500KL GLSR |  |  |  | 1No | 1
9 | Supply and Fixing of SS Railing containing vertical size 40mm thickness 16 gauge at height 1.10M and top horizental pipes 40mm size and thickness 16 gauge and middle 25mm size thickness 16 gauge and including base covers and L Bends and Dummys as per standard requirements including cost and conveyance of all labour charges etc., complete, except GST
i | For 500KL ELSR |  |  |  | 1Rmt | 100
ii | For 500KL Sump |  |  |  | 1Rmt | 45
iii | For Staircase |  |  |  | 1Rmt | 135

## GLSR
Construction of sump 500KL
Plastering Details for 500KL Sump Plastering Details
S.no | Description | No's |  |  | L | B | Qty(m2) | Remarks
5 | Plastering for Sump
| Sump Bottom Raft Plastering | 1 | X | 3.14 | 6.5 | 6.5 | 132.67
| Sump Sidewall Inside Plastering | 1 | X | 3.14 | 13 | 4 | 163.28
| Column Plastering Near Wall 8 Columns | 8 | X | 3 | 4 | 0.3 | 28.8
| Sump top slab top side plastering | 1 | X | 3.14 | 6.9 | 6.9 | 149.5
| Top slab patti | 1 | X | 3.14 | 13.8 | 0.15 | 6.5
[5 empty] | Total Qty |  | 480.75 | Sqm
Plastering Details for 500KL Sump Painting Details
S.no | Description | No's |  |  | L | B | Qty(m2) | Remarks
5 | Painting for Sump
| Sump Bottom Raft Painting | 1 | X | 3.14 | 6.5 | 6.5 | 132.67
| Sump Sidewall Inside Painting | 1 | X | 3.14 | 13 | 4 | 163.28
| Column Painting Near Wall 8 Columns | 8 | X | 3 | 4 | 0.3 | 28.8
| Sump top slab top side Painting | 1 | X | 3.14 | 6.9 | 6.9 | 149.5
| Sump inner column painting | 4 | X | 4 | 4 | 0.3 | 19.2
| Top slab patti Painting | 1 | X | 3.14 | 13.8 | 0.15 | 6.5
[5 empty] | Total Qty |  | 499.95 | Sqm
Supplimentary Items in Sump
10 | Manfacturing supply delivery lowering laying jointing testing of MS pipe using 8mm thick MS piate including cost and conveyanc of all material and cost oe epoxy painting labour charges and all incidental operation charges complete
i | A)150mm Dia MS Pipe |  |  |  | 1Rmt | 30
ii | B)250mm Dia MS Pipe |  |  |  | 1Rmt | 5
11 | Manfacturing supply delivery lowering laying jointing testing of MS pipe using 8mm thick MS piate including cost and conveyanc of all material and cost oe epoxy painting labour charges and all incidental operation charges complete
i | A)400mm Dia MS Pipe |  |  |  | 1Rmt | 15
12 | Manufacture, Supply, & Delivery of HDPE fittings conforming to IS 4984 - 1995 including transportation to anywhere in T.G. Excluding taxes
A) MS Flanges
i | 150mm Dia |  |  |  | 1No | 2
ii | 250mm Dia |  |  |  | 1No | 1
iii | 400mm Dia |  |  |  | 1No | 3
13 | Manifacture, Supply and Delivery of R.C.C Spun / Vibrated cast (Reinforced) Socket and Spigot pipes conforming to B.I.S. 458/2003, Cost of Rubber Ring,transportation charges and Including Labour Charges for lowering ,laying,jointing in readymade trenches true to alighenment and Gradient and all incidental operation charges etc complete
[5 empty] | 1Rmt | 30
[9 empty] | 0 | 0 | 0 | 0
0

## Pipeline
PROVIDING DISTRIBUTION NETWORK SYSTEM
Supplimentary
14 | Supply and Fixing of pre-cast RCC Chamber bottom size width 36' Dia and top 21' Dia over CC Bed (1:4:8) including cast and conveyance all material labour charges and incidental charges etc complete
| For Sluice Valve | 1NO | 30 | 30
15 | Supply and fixing M.D -10 with 560mm dia clear opening C.I. Manhole frame and cover for 914.4 mm dia chamber (20 Kg- light weight) in the roof of the Sump as shown in the detail drawing with a clear opening of 760 mm dia including cost and conveyance of all materials to site, all labour charges, complete as directed by Engineer-in-Charge for finished item work, except GST.
| For Sluice Valve | 1NO | 30 | 30
16 | Re filling foundation/ basement /pipe line trenches with useful excavated soils (other than black cotton soils and other expansive soils) with initial lead and lifts spreading in layers not exceeding 150mm thick, consolidating each deposited layer by watering and ramming, compacting by earth mover to achieve optimum moiture content including cost and conveyance of water to work site and all operational, incidental, all labour charges, hire charges of T&P etc., complete for finished item of work, as directed by Engineer-in-charge (APSS No. 309 & 310), except GST. (Total Excavation-Deduct Raft Foundation Qtys=768.46-128.65=639.81)
|  | 1Cum | 8925 | 8925
17 | Centrifugally cast (span) Ductile Iron Fittings conforming to IS:9523/2000 having dimensions as per table. The rates mentioned here under are for fitting,zinc coated externally with inside mortor lining (with finishing as per class 13/IS 9523/2000) (ex-works) Excluding Tranportation and Taxes
|  | 1KG | 1050 | 1050
18 | Manifacturing supply delivery of Air valve gauge fabrication of size 1x1x1m using 50x50x6mm MS angles vertical and horizental frame and fixing 10mm squre rods c/c 150mm including cost and convenyance of all material and cost epioxy paint labour charges and fixing gauge in cement concrete morter and allincidental operation etc complete.
|  | 1 No | 17 | 17
19 | Plain Cement concrete (M 20) grade using 20mm and 10mm metal using concrete mixer nominal size well graded machine crushed granite stone chips from approved quarry including cost and conveyance and seigniorage charges of all materials like cement, sand coarse aggregate, water etc., to site, cost of seigniorage on materials including centering, shuttering machine mixing, laying concrete, tamping finishing smooth to required levels, curing mall other incidental and operational charges, labour charges etc., complete but excluding cost of steel and its fabrication charges for the following finished item of work.
i | CC Road Concrete for Pipeline restoring of roads | 1Cum | 30 | 30
20 | Manufacture, Supply, & Delivery of HDPE fittings conforming to IS 4984 - 1995 including transportation to anywhere in T.G. Excluding taxes
i | MS Flanges to suit HDPE Pipes for
| 225 mm dia HDPE 6Kg/Cm2 pipe | 1No's | 20 | 20
ii | Tees for
| 225 mm dia HDPE 6Kg/Cm2 pipe | 1No's | 9 | 9

## Panal board
Construction of Panal Board
S.no | Description | No |  |  | L | B | D | QTY | Unit
21 | Earth work excavation by Mechanical means for Sump/OHT/Pump Room & Pipe Line trenches and depositing on bank in all types of soils like morum, red earth, gravely soils, ordinary soils upto SDR in all conditions including hire & operational charges of machinery, labour charges for setting out, construction of shoring and bracing, removal of stumps and all other deletarious matter, dressing on sides & bottom of trench in all conditions viz dry, wet and slushy etccomplete for finished item of work as per SS 20 B (APSS 308), except GST.
| a)columns | 1 | X | 6 | 2 | 2 | 2 | 48
| b)For Basement | 1 | X | 6 | 33.83 | 0.5 | 0.7 | 71.04
| c)For septic tank | 1 | X | 1 | 2.5 | 1.65 | 2 | 8.25
[8 empty] | 127.29 | Cum
| Deduct Rock Volume 23% | [6 empty] | 29.2767
[8 empty] | 98.0133 | Cum
22 | Earthwork Excavation in Hard Rock
| Qty As per Item No 1 Deduct Volume | [6 empty] | 29.2767 | Cum
23 | Plain Cement Concrete (1:4:8) prop.using 40mm nominal size well graded hard broken granite metal from approved quarry including cost and conveyance of all material, all labour charges for machine mixing of concrete, laying concrete, compacting by vibration including curing, finishing top surface to required levels neatly etc., complete as derected by Engineer-in-charge for finished item of work in foundations, excluding GST & seigniorage charges.
1 | PCC (1:4:8) | 1 | X | 6 | 1.5 | 1.5 | 0.15 | 2.03
Above Basement PCC
| PCC (1:4:8) | 1 | X | 1 | 16.83 | 0.6 | 0.1 | 1.01
| PCC (1:4:8) | 1 | X | 1 | 17 | 0.6 | 0.1 | 1.02
| PCC (1:4:8) | 1 | X | 1 | 6.83 | 0.38 | 0.1 | 0.26
| PCC (1:4:8) | 1 | X | 1 | 27 | 0.45 | 0.1 | 1.22
| PCC (1:4:8) | 1 | X | 1 | 8.5 | 5 | 0.15 | 6.38
| Septic Tank pcc | 1 | X | 1 | 2.5 | 1.65 | 0.15 | 0.62
[6 empty] | Total Qty |  | 12.54 | Cum
24 | Providing and laying of Vibrated Reinforced Cement Concrete corresponding to M-30 grade Design Mix Concrete corresponding to IS 456 using weigh batcher with 20mm size well graded machine crushed hard granite chips (Coarse aggregate) from approved quarry with a minimum cement content of 400 kg/CuM including cost and conveyance of all materials like cement, Coarse aggregate, Fine aggregate, water etc., to site, weigh batcher, machine mixing, laying concrete, vibrating, finishing smooth to required levels, curing, pumping to work spot, lifting of material with mechanical equipment like winch, etc., all other incidental and operational charges, all labour charges, etc., but excluding cost of centering & shuttering, cost of steel and its fabrication charges complete as directed by Engineer-in-Charge for the following finished item of work, excluding GST & seigniorage charges.
i | Footing Concrete | 1 | X | 6 | 1.2 | 1.2 | 0.3 | 2.59
ii | Column Concrete upto Roof level | 1 | X | 6 | 0.3 | 0.3 | 4.5 | 2.43
iii | Plinth Beam Concrete
| Long Beam EPB1 | 1 | X | 2 | 0.23 | 0.3 | 8.5 | 1.17
| Short Beam EPB1 | 1 | X | 2 | 0.23 | 0.3 | 5 | 0.69
| Short Beam IPB1 | 1 | X | 1 | 0.23 | 0.3 | 5 | 0.35
| Short Beam IPB1 | 1 | X | 1 | 0.23 | 0.3 | 1.83 | 0.13
iv | Roof Beam and Slab Concrete
| Long Beam Concrete (B1) | 1 | X | 2 | 0.23 | 0.3 | 8.5 | 1.17
| Short Beam Concrete (B1) | 1 | X | 3 | 0.23 | 0.3 | 5 | 1.04
| Slab Concrete | 1 | X | 1 | 8.5 | 5 | 0.125 | 5.31
| Septic Tank Slab | 1 | X | 1 | 2.5 | 1.65 | 0.1 | 0.4125
[8 empty] | 15.2925 | Cum
25 | Centring and Scaffolding charges for RCC members including all materials and Labour charges for forming and removing etc., complete as directed by Engineer-in-Charge for finished item of work. Except GST
| a)Columns | 6 | x | 4 | 0.3 | 3.7 | 26.64
| b)Plinth Beam | 1 | x | 1 | 33.83 | 0.83 | 28.08
| c)Roof Beam | 1 | x | 1 | 32 | 0.6 | 19.2
| d)Roof Slab | 1 | x | 1 | 8.5 | 5 | 42.5
[7 empty] | 116.42 | Sqm
26 | Providing High Yield Strength Deformed (HYSD)/ Thermo Mechanically Treated (TMT) steel bars (Fe 415 grade as per IS 1786-1979) upto 36mm dia for RCC and RCM works including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and size and tying and lap-splicing with binding wire of 18 SWG, forming grills for reinforcement work as per approved designs and drawings including cost and conveyance of steel bars including all wastages such as overlaps, couplings, chairs, spacer bars including cost and conveyance of binding wire, cover blocks and all incidental, operational, all labour charges such as cutting, bending, placing in position, tying etc., complete for finished item of work, as directed by Engineer-in-Charge (APSS No.126), excluding GST and seignorage charges.
| Qty item no 4 at 16cum@130kg/1cum | [6 empty] | 3 | MT
27 | Re filling foundation/ basement /pipe line trenches with useful excavated soils (other than black cotton soils and other expansive soils) with initial lead and lifts spreading in layers not exceeding 150mm thick, consolidating each deposited layer by watering and ramming, compacting by earth mover to achieve optimum moiture content including cost and conveyance of water to work site and all operational, incidental, all labour charges, hire charges of T&P etc., complete for finished item of work, as directed by Engineer-in-charge (APSS No. 309 & 310), except GST.
| Earthwaork Excavation Qty | [6 empty] | 128
| Basement Filling Qty | 1 | x | 1 | 8.5 | 5 | 0.6 | 25.5
153.5
Deductions
| PCC (1:4:8) | [6 empty] | 15.54
| For Basement | [6 empty] | 13.7
| For Footing | [6 empty] | 2.59
31.83
[6 empty] | Net Qty |  | 121.67 | Cum
28 | RR masonry in CM (1:6) using hard granite stone from approved quarry including cost and conveyance, seigniorage of all materials, water, all labour charges for dressing stones to required size and shape mixing of cement mortar, wall construction,scaffolding charges, etc., excluding GST, Complete for finished item of work
| For Basement | 1 | x | 1 | 33.83 | 0.45 | 0.9 | 13.7
29 | Brick Masonary in CM (1:6) With 2nd class Clay Bricks traditional size 23x11x11cms including cost and conveyance of all material labour charges and incidental operational charges etc complete
| A)LW | 1 | X | 2 | 8.5 | 0.225 | 3.1 | 11.86
| B)SW | 1 | X | 3 | 5 | 0.23 | 3.1 | 10.7
|  | 1 | X | 1 | 1.83 | 0.23 | 3.1 | 1.3
| C)Parapit wall | 1 | X | 1 | 27 | 0.23 | 1 | 6.21
| F)Septic tank walls | 1 | X | 1 | 7.32 | 0.23 | 2 | 3.37
[8 empty] | 33.44 | Cum
Deductions
| a)Doors D1 | 1 | X | 2 | 1 | 0.23 | 2 | 0.92
| b)Doors D2 | 1 | X | 2 | 0.75 | 0.23 | 1.8 | 0.62
| c)Windows | 1 | X | 4 | 1.5 | 0.23 | 1.2 | 1.66
| d)Ventiletors | 1 | X | 2 | 0.6 | 0.23 | 0.3 | 0.08
| e)Lintals over Doors D1 | 1 | X | 2 | 1.3 | 0.23 | 0.15 | 0.09
| f)Lintals over Doors D2 | 1 | X | 2 | 1 | 0.23 | 0.15 | 0.07
[8 empty] | 3.44 | Cum
[6 empty] | Net Qty |  | 30 | Cum
30 | Supply & fixing of Rolling shutter made of 80x1.25 mm machine rolled CRCA laths, interlocked together through their entire length and jointed together at the ends by end-locks, mounted on specially designed pipe shaft of 50mm Diameter nominal bore MS B class pipe with brackets, plates, guide channels, stoppers, bottom locking plates andarrangements for inside & outside locking with push-pull operations including cost of hood cover and springs complete, painted with one coat of approved steel primer, locks, ball bearings, all accessories etc complete for finisheditemofworkasperspecialSpec:110, Excluding GST
|  | 1Sqm |  | 8.06 |  |  |  | 8.06
31 | Plastering with 12mm thick in single coat in CM (1:4) finished smooth including cost and conveyance of all materials to site, finishing, curing, scaffolding and all operational, incidental, labour charges etc., including cutting grooves where ever necessary etc., complete for finished item of work as directed by Engineer-in-Charge, excluding GST (As per SS 903).
Inside
| Room sides | 2 | X | 2 | 8.5 | 3.1 | 105.4
|  | 1 | X | 4 | 5 | 3.1 | 62
|  | 1 | X | 2 | 1.83 | 3.1 | 11.35
Outside
| LW | 1 | X | 2 | 8.5 | 3.1 | 52.7
| SW | 1 | X | 2 | 5 | 3.1 | 31
| Parapit wall | 1 | X | 2 | 27 | 1 | 54
| Septic Tank | 1 | X | 1 | 6.4 | 2 | 12.8
| Baement outide plastering | 1 | X | 1 | 27 | 0.6 | 16.2
345.45
Deductions
| A)Doors | 2 | X | 4 | 1 | 2 | 16
| B)Windows | 2 | X | 4 | 1.5 | 1.2 | 14.4
| C)Ventilaters | 2 | X | 2 | 0.6 | 0.3 | 0.72
31.12
[5 empty] | Net Qty |  | 314.33 | Sqm
32 | BLD-CSTN-13-16 - Supply and fixing Teak Wood framed FLUSH Doors single shutter door with flush shutter as per approved drawings with best quality 2nd class teakwood frame od size 115x65mm and flush door shutters of 30 mm thick solid bond wood block board typer with teak veneer on one face and commercial ply on another face (One side Teak) teak wood internal lipping as per drawing including fixing of 6 Nos. MS Z hold fasts of size 300 x 40 x 5mm size including cost of Powder Coated/ Chromium Plated Mild Steel fixtures of 3 Nos. butt hinges 150 x 31.75 x 3.5 mm, 2 No tower bolt of 250x12mm dia, 1 No.CP Aldrops - 300 mm long and 2 Nos. CP handles of 150 mm size & 1 No. 63 mm long door stopper including fixing the fixtures to door with required no. of brass screws, bolts and nuts including labour charges for fixing the frame in position, fixing the shutter to the frame etc., complete for finished item of work as per APSS 1001 & 1002 (0.90x2.15)
| A)Doors D1 |  |  | 1X4 | 1 |  | 2 | 8
| B)Doors D2 |  |  | 1X2 | 0.75 |  | 1.8 | 2.7
[8 empty] | 10.7 | Sqm | 5470.34 | 1Sqm | 58532.638
33 | Ceramic wall tiles supply of glazed red or white fully body ceramic wall tilws of size 200 x 300 mm /245 mm x 325 mm and thickness 6mm 1st quality, set over CSTN-9- over a base coat of cement mortar (1:8) prop., 12 mm thick and filling the joints with 3mm Nylon spacers at each corner of the tile and joints grooted with laticrete epoxy grout of pigment of approved shade of tiles over a wall. or R.C.C. slab, including cost and conveyance of all materials like cement, sand, water, tiles, white cement etc., to site (excluding cost of C.C. bed) cost of excluding seigniorage on all materials cost of base coat and all labour charges for mixing of cement mortar, laying tiles to required slope as directed by the Ebgineer-in-charge curing etc., complete for finished item of work, IS 13711, IS:13712 IS 13713
| a)Both Room |  |  | 1x1 | 5.4 |  | 1.5 | 8.1
| b)WC |  |  | 1X1 | 5.1 |  | 1.5 | 7.65
[8 empty] | 15.75 | Sqm
34 | Painting to new walls with two or more coats of Water proof cement paint of approved make, shade and colour to give uniform shade to all plastered surfaces of walls over a base coat of approved cement, primary grade making 3 coats of white cement (total 3 or more coats) in all to give an even shade after thoroughly brushing the surface to remove all dirt and remains of loose powedered materials including cost and conveyance of all materials to work site, and all labour charges such as preparation of the wall surface, applying priming coat, applying water proof cement paint two or more coats, curing, scaffolding etc., complete as directed by Engineer-in-Charge for finished item of work as per SS 912, except GST.
Inside
| Room sides | 2 | X | 2 | 8.5 | 3.1 | 105.4
|  | 1 | X | 4 | 5 | 3.1 | 62
|  | 1 | X | 2 | 1.83 | 3.1 | 11.35
Outside
| LW | 1 | X | 2 | 8.5 | 3.1 | 52.7
| SW | 1 | X | 2 | 5 | 3.1 | 31
| Parapit wall | 1 | X | 2 | 27 | 1 | 54
| Septic Tank | 1 | X | 1 | 6.4 | 2 | 12.8
| Baement outide plastering | 1 | X | 1 | 27 | 0.6 | 16.2
345.45
Deductions
| A)Doors | 2 | X | 4 | 1 | 2 | 16
| B)Windows | 2 | X | 4 | 1.5 | 1.2 | 14.4
| C)Ventilaters | 2 | X | 2 | 0.6 | 0.3 | 0.72
31.12
[5 empty] | Net Qty |  | 314.33 | Sqm
35 | Providing imperious / weather proof coarse over RCC roof slabs with CM (1:3) with an average thickness of 20mm thick premixed with water proofing compound like ACCO proof or any other ISI make at one KG per bag of cement as prescribed by the manufacturer and laid over the proof slab to required slopes as directed by the engineer in charge when slab is in green including cost and conveyance of all material to site all labour charges and for all operation maintaining necessary slope finishing smooth and lining curing etc complete
| A)RCC slab Roof and Bottom | 1 | x | 2 | 8.5 | 5 |  | 85 | Sqm
36 | Supplying and fixing of Unplasticised Poly Vinyl Chloride (UPVC) sliding windows two track sliding duly manufactured using UPVC reinforced profiles of (62 mm x 60 mm)/(60 mm x 45 mm) / (60 mm x 52 mm) x 2.0 mm for outer frames, (66 mm x 38 mm) / (58 mm) x 39 mm)/ (60 mm x 42 mm) x 2.0 mm for sliding shutter frames capable of mounting single glazing system, structurally reinforced with hot dip galvanized up to 50 micros of minimum thickness of 1.2 mm prefabricated & welded through fusion welding the window sash shall be fitted with 5 mm thick clear float glass of reputed make duly fixed with TPV Gaskets/EPDM weathering seal resistant accessories like locking system 1 No., per set of sashes and the system is to be installed at the site using anchor fasteners, silicon rubber sealent, easy glazing/ deglazing at site etc., including cost and conveyance of all materials, accessories, labour charges for transportation, erection at site with templates for casement sizing complete for finished item of work.
| A)Windows | 1 | X | 4 | 1.8 |  | 1.5 | 10.8 | Sqm
SANITARY ITEMS
37 | Supplying laying jointing and testing 101.6mm SWG SP-1 pipes of ISI Make confirming to ISI 651 & 4127 with airtight cement joints in CM 1:5:1 prop. Including excavation of trenches and socket pits in any soil(except rock requiring blasting) upto 914.4 mm(3"0') depth and refilling with watering and tamping
|  | 1 | X | 1 | 40 |  |  | 40 | Rmt
38 | Supplying and fixing 150 mm x 100 mm SWG gully traps confirming to ISI 651 & 4127 with C.I. grating & Cost brick masonry in CM 1:6 prop.. Intermediate chamber and fitted with 304.8mm x 288.6mm (12"x9") C.I. Frme and hinged cover.
|  | 1 | X | 1 |  |  |  | 1 | Nos
39 | Constructing 904.0mm (3"0') dia solid brick masonry inspection chamber as per IS - 4111: Part-1: 1986 with cement mortar (1:6) prop. Using 2nd class clay bricks of 225mm thick from approved source having a minimum crushing strength of 5 N/ Sq.mm including plastering with cement mortar 1:3 prop; 1/2" thick both inside and outside fitted with 20" dia RCC Manhole covers and frames including excavating pits upto a depth of 904mm (3'-0") in all sorts of soils ( excluding rock) and laying cement concrete (1:4:8) 150mm thick using 40mm HBG Metal and PCC 1:2:4 benching and channel 100 mm thick as per standard specification and including cosrt and conveyance of all materials like cement,sand , bricks, water etc.m, to site, cost of seigniorage charges on all materials and all incidentall and operational, labour charges like mixing cement mortar , constructing masonry, lift charges curing, etc., complete for finished item of work as per standard specification.
|  | 1 | X | 3 |  |  |  | 3 | Nos
40 | Supply and fixing of approved make Orissa pan white glaze W.C. ist quality ISI Marked confirming to IS:2556 -Part-3-2004 with "P" or "S" Trap : 580mm x 440mm duly provading construction brick masonry and CC squatting plate including cost and conyence of all materials and labour charges etc complete as per standard practice for finished item.
|  | 1 | X | 1 |  |  |  | 1 | Nos
41 | Supplying and fixing low down porcelain flushing tank with lid 10Lit capacity with internal components
|  | 1 | X | 1 | 1 |  |  | 1 | Nos
42 | Supplying and fixing Indian make Flat Back Wash Hand Basin 1st quality confirming to IS: 2556-Part-4:1972 with waste fittings like rubber plug , chain, 32mm nominal size C.P. Fitting with parallel pipe thread confirming to IS: 2963-1979 and fitted with 15mm nominal bore Chromium Plated Pillar Tap og 1st quality Indian make 400 grams complete with standard CI Brackets including wooden block : 630x 450mm - Single C.P. Pillar cock
|  | 1 | X | 1 | 1 |  |  | 1 | Nos
43 | Supply and fixing of 90mm dia single socket PVC/SWR Pipe- 4kg/sqm including cost and conveyance of all material labour charges etc.,
|  | 1 | X | 1 | 15 |  |  | 15 | Rmt
44 | Supply of rubber lubricant 500 grams UPVC/SWR Pipe fittings
|  | 1 | X | 1 | 1 |  |  | 1 | Nos
45 | S&F 20 mm Nominal Bore GI Pipe Medium grade properties & weight as per IS 1239 ISI Markwith GI Fittings including the cost of pipe and its fittings & labour charges complete
|  | 1 | X | 1 | 10 |  |  | 10 | Rmt
46 | S&F 25 mm Nominal Bore GI Pipe Medium grade properties & weight as per IS 1239 ISI Markwith GI Fittings including the cost of pipe and its fittings & labour charges complete
|  | 1 | X | 1 | 30 |  |  | 30 | Rmt
47 | S&F of 15mm brass body CP finish bib tap of not less than 300 grams weight with quarter turn spindle with either internal or external threaded connection confirming to IS 8931
|  | 1 | X | 3 | 3 |  |  | 3 | Nos
48 | S&F of 15mm brass body CP finish pillar tap of not less than 300 grams weight screw type(full turn) confirming to IS 8931
|  | 1 | X | 1 | 1 |  |  | 1 | Nos
49 | S&F of 15mm brass angle stop valve of qurter turn spindle type of not less than 400 grams weight with internal threaded connection confirming to IS 8931
|  | 1 | X | 2 | 2 |  |  | 2 | Nos
50 | Supplying and fixing of 15mm nom,inal size PVC Connection with brass union nut C.P. Coated
|  | 1 | X | 2 | 2 |  |  | 2 | Nos
51 | Providing & Placing on terrace ( at all floor levels) polyethylene water storage tank with Double layer approved brand & manufacture with cover and suitable locking arrangement & making necessary holes for inlet & outlets and overflow pipes but without fittings & base support for tanks
|  | 1 | X | 1 | 500 |  |  | 500 | Litres
52 | Supplying & Fixing white glazed flat back half stall urinals 1st quality conforming to IS:2556-1995 with standard C.P. Spreader fixed with screws complete Indian make : 590 x 375 x 390 mm
|  | 1 | X | 4 | 4 |  |  | 4 | Nos
Cost and Erection of Pumps and Motors With Electrical Panal Board
53 | Supply, delivery and fixing of 20 HP 3 phase 415 Volts submersible monoblock horizontle booster pump set with a Head of 25 Mts. to discharge 37LPS of Lubi/texmo including cost and conveyance of all materials and labor charges etc complete as directed by the TSSC Engineers. |  |  |  | 1No | 2 |  | 2 | 1No
54 | Supply, delivery and laying of 4 core, 4 sq mm, Copper armored underground cable finotex make from outdoor panel to pump set near MS shell including necessary connection with cost and conveyance of taxes duties with all other incidental and operational charges etc. complete as directed by the TSSC Engineers. |  |  |  | 1Rmt | 26 |  | 26 | 1Rmt
55 | Supply fabrication of suitable outdoor panel with enamel coated in 16 SWG iron sheet comprising of below items internal wiring with necessary locking arrangements as mentioned below for 1 No. 20 HP open well submersible pump set of L&T/BCH of its equivalent make a) 32 Amps contactors 3 No. b) Suitable relay 1 No.c) Suitable Timer 1 No d) 100 amps MVVB of 35 KVA 1 No e)32 amps MCB for capacitor 1 No f) 0-500 Volts voltmeter Digital 1 No. g) 0-60 amps Ammeter Digital 1 No h) Capacitor 15 KV. AR 1 No. i) RYB indication lamps 1 set etc., complete as directed by the TSSC Engineers. |  |  |  | 1Set | 2 |  | 2 | 1Set
56 | Supply, Transportation and Installation of 150mmx50mmx1.6mm thick hot dip GI perforated cable tray without cover along with coupler plates, Anchor bolts and nuts etc complete and the tray should be fitted on the wall / Ceiling etc. complete for finished item of work. |  |  |  | 1Rmt | 30 |  | 30 | 1Rmt
57 | Supply and fixing air vessel made of 250 mm dia, 8 mm thick MS sheet, 1200mm in height with air release valve on top and flanged connection to riser, drain arrangement with 25mm dia Gun metal wheel valve, with required accessories, pressure gauge and painting with synthetic enamel paint of approved shade as required. |  |  |  | 1No | 1 |  | 1 | 1No
58 | Manufacture, Supply and delivery of 150 Dia DI D/F Gate Valves (Soft Seated) Resilient seated soft sealing gate valves (Sluice valves) with body bonnet of ductile cast iron of grade GGG-40/ SG- 400/15 or GGG-50/SG-500/7 or equivalent grade as per I.S.3896-part2-1985 and subsequent revisions, wedge fully rubber lined with EPDM food grade quality and seals of NBR and the valves should be of vacuum tight and 100% leak proof with face to face dimensions as per BS5163-89/IS14846-2000/DIN 3202 F 4. All the valves should be with Electrostatic powder coating both inside and outside pocket less body passage. Drilled as per requirement of the dept |  |  |  | 1No | 2 |  | 2 | 1No
59 | Supply and delivery of 150mm dia CI D/F Non return valve heavy duty round body conforming IS 5312/part 1/1984, including all taxes duties etc., complete the valves shall be tested requirement ISI make labor charges etc complete as directed by the TSSC Engineers. |  |  |  | 1No | 2 |  | 2 | 1No

## General Abstract
Work Slip
Name of Work:Providing water supply Facilities to Electronic Hardware Manifacturing Cluster at Maheswaram (V & M) RR Dist
S.No | Description | Amount of Sanction (RS) | As Per execution | Excess | Less | Remarks
1 | CIVIL WORKS |  |  |  |  | Including All Authorized extras & Supplimental items
A) | Construction of 500KL Capacity of sump | 3156905.34
B) | Construction of 500KL Capacity over head tank | 9773049.31
C) | Providing distribution network system | 16544699.76
D) | Construction of Panal Board Room
|  | 29475000 | 32258271.7519 | 2783271.7519
2 | LS Provision
A) | DI Fittings | 1500000 |  |  | 1500000
B) | Erection of Pumpsets | 500000 |  |  | 500000
C) | Provision per PS & Contingencies @ 1.5% | 443000 | 443000 |  | 443000
D) | Provision per Prise adjestiment@ 5% | 1474000 | 806456.7938 |  | 667543.2062
E) | Provision per Quality control @ 0.5% | 148000 | 148000 | 0
F) | Provision per Tender Premium @5% | 1474000 |  |  | 1474000
G) | NAC @0.1% | 30000 | 32258.2718 | 2258.2718 |  |  | 47.04
H) | seigniorage Charges | 119722.48 | 130000 | 10277.52
I) | Provision per GST@12% | 3555000 | 3870992.6102 | 315992.6102
J) | Provision per unforseen item @2% | 781277.52 | 311020.57 |  | 781277.52
|  | 39500000 | 37999999.9976 | 3111800.1538 | 5365820.7262
| As per Sanction Estimate Amount Of RS | 39500000
| As per Workdone Of RS | 37999999.9976
| Less over The Estimate RS | 1500000.0024
| Less over The Estimate TP | 3.7975 | %
Project Engineer |  | Dy Zonal manager(E) |  | Zonal manager
TSIIC Ltd, Shamshabad Zone |  | TSIIC Ltd, Shamshabad Zone |  | TSIIC Ltd, Shamshabad Zone

## FIS
Name of Work:Providing water supply Facilities to Electronic Hardware Manifacturing Cluster at Maheswaram (V & M) RR Dist
FINANCIAL IMPLICATION STATEMENT
Agt | Discription of item | As per Agreement |  |  |  | As per Execution
.No. |  | Quantity | Unit | Rate Per | Total value | Quantity | Rate/ per | Total value | Excess | Less | Remarks
Construction of 500 KL Capacity Over Head Tank
1 | Earth work excavation by Mechanical means for Sump/OHT/Pump Room & Pipe Line trenches and depositing on bank in all types of soils like morum, red earth, gravely soils---- | 330 | Cum | 101.04 | 33343.2 | 330 | 101.04 | 33343.2
| Authorized extra |  |  |  |  | 420.57 | 101.04 | 42494.39 | 42494.39 |  | As Per Deviated Approved Drawing
2 | Plain Cement Concrete (1:4:8) prop.using 40mm nominal size well graded hard broken granite metal ---- | 22 | Cum | 4142.08 | 91125.76 | 22 | 4142.08 | 91125.76 |  |  |  | 58.27
| Authorized extra |  |  |  |  | 36.27 | 4142.08 | 150233.24 | 150233.24 |  | As Per Deviated Approved Drawing | 29.25
3 | Providing and laying of Vibrated Reinforced Cement Concrete corresponding to M-30 grade Design Mix Concrete corresponding to IS 456 using weigh batcher with 20mm ---
i | Bottom raft slab | 52 | Cum | 8785.93 | 456868.36 | 52 | 8785.93 | 456868.36
| Authorized extra |  |  |  |  | 40.09 | 8785.93 | 352227.93 | 352227.93 |  | As Per Deviated Approved Drawing
ii | Raft beam below plinth level | 6 | Cum | 11049.14 | 66294.84 | 6 | 11049.14 | 66294.84
iii | Footings of OHT & Stair case | 3.1 | Cum | 8785.93 | 27236.38 | 3.1 | 8785.93 | 27236.38
| Authorized extra |  |  |  |  | 2.08 | 8785.93 | 18274.73 | 18274.73 |  | As Per Deviated Approved Drawing
iv | Pedastal | 4.3 | Cum | 9255.16 | 39797.19 | 2 | 9255.16 | 18510.32 |  | 21286.868
v | Tie beam below ground level | 10.6 | Cum | 11049.14 | 117120.88 | 0 | 11049.14 | 0 |  | 117120.884
4 | Providing and laying of Vibrated Reinforced Cement Concrete corresponding to M-30 grade Design Mix Concrete corresponding to IS 456 using weigh batcher with 20mm size ----
A | OHT -Columns (below bottom slab- size: 500mm x 500mm & Above bottom slab- size: 500mm x 500mm) & stair case column -500mm dia.
i | above Plinth Level and up to 3.0 mt level | 11 | Cum | 8191.7 | 90108.7 | 6.46 | 8191.7 | 52918.38 |  | 37190.318
ii | Above 3.0 mt and Up to 6.0mt level | 10 | Cum | 8375.76 | 83757.6 | 10 | 8375.76 | 83757.6
| Authorized extra |  |  |  |  | 8.01 | 8375.76 | 67089.84 | 67089.84 |  | As Per Deviated Approved Drawing
iii | Above 6.0 mt and Up to 9.0mt level | 10 | Cum | 8559.81 | 85598.1 | 10 | 8559.81 | 85598.1
| Authorized extra |  |  |  |  | 6.54 | 8559.81 | 55981.16 | 55981.16 |  | As Per Deviated Approved Drawing
iv | Above 9.0 mt and Up to 12.0mt level | 10 | Cum | 8743.87 | 87438.7 | 10 | 8743.87 | 87438.7
| Authorized extra |  |  |  |  | 6.54 | 8743.87 | 57184.91 | 57184.91 |  | As Per Deviated Approved Drawing
v | Above12 mt and upto15.00 Mts level | 12.1 | Cum | 8927.93 | 108027.95 | 12.1 | 8927.93 | 108027.95
| Authorized extra |  |  |  |  | 4.17 | 8927.93 | 37229.47 | 37229.47 |  | As Per Deviated Approved Drawing
vi | Above15 mt and upto18.00 Mts level | 0.2 | Cum | 9111.98 | 1822.4 | 0.2 | 9111.98 | 1822.4
| Authorized extra |  |  |  |  | 2.5 | 9111.98 | 22779.95 | 22779.95 |  | As Per Deviated Approved Drawing
B | Beams (Braces)
i | Lower Braces-tie beam-below GL | 9.5 | Cum | 9263.09 | 87999.36 | 0 | 9263.09 | 0 |  | 87999.36
ii | Brace -From GL upto 3.00Mts | 9.5 | Cum | 5955.76 | 56579.72 | 9.5 | 5955.76 | 56579.72
| Authorized extra |  |  |  |  | 21.1 | 5955.76 | 125666.54 | 125666.54 |  | As Per Deviated Approved Drawing
iii | Brace -above 3.00mts and upto 6.00mts | 9.5 | Cum | 6139.81 | 58328.2 | 9.5 | 6139.81 | 58328.2
| Authorized extra |  |  |  |  | 5.8 | 6139.81 | 35610.9 | 35610.9 |  | As Per Deviated Approved Drawing
iv | Brace -above 6.00mts and upto 9.00mts | 9.5 | Cum | 6323.87 | 60076.77 | 9.5 | 6323.87 | 60076.77
| Authorized extra |  |  |  |  | 5.8 | 6323.87 | 36678.45 | 36678.45 |  | As Per Deviated Approved Drawing
v | Brace -9.00mts and upto 12.00mts | 9.5 | Cum | 6507.92 | 61825.24 | 0 | 6507.92 | 0 |  | 61825.24
vi | Brace -12.00mts and upto 15.00 mts (Ring beam) | 9.5 | Cum | 6691.98 | 63573.81 | 0 | 6691.98 | 0 |  | 63573.81
vii | Brace -above 12.00mts and upto 15.00 mts -At a height of 14.50m from GL | 14 | Cum | 6691.98 | 93687.72 | 0 | 6691.98 | 0 |  | 93687.72
C | Beam at Bottom slab - at 14.50m from GL | 8.2 | Cum | 6691.98 | 54874.24 | 8.2 | 6691.98 | 54874.24
| Authorized extra |  |  |  |  | 23.83 | 6691.98 | 159469.88 | 159469.88 |  | As Per Deviated Approved Drawing
D | Bottom slab at 14.50m from GL | 39 | Cum | 6691.98 | 260987.22 | 38.54 | 6691.98 | 257908.91 |  | 3078.3108
E | Internal Columns in the tank above 15.00mts and upto 18.00 mt | 2.9 | Cum | 9111.98 | 26424.74 | 2.23 | 9111.98 | 20319.72 |  | 6105.0266
F | Side Wall | 25.5 | Cum | 9296.04 | 237049.02 | 25.5 | 9296.04 | 237049.02
| Authorized extra |  |  |  |  | 25.41 | 9296.04 | 236212.38 | 236212.38 |  | As Per Deviated Approved Drawing
G | Beam at Roof slab | 7 | Cum | 6876.04 | 48132.28 | 0 | 6876.04 | 0 |  | 48132.28
H | Inner Beams in Tank at roof level -a height of 18.45 M from GL | 12 | Cum | 6876.04 | 82512.48 | 3 | 6876.04 | 20628.12 |  | 61884.36
I | Roof Annular Slab | 29 | Cum | 6876.04 | 199405.16 | 25 | 6876.04 | 171901 |  | 27504.16
5 | Centering and scaffolding charges for RCC members including all materials and labour charges for forming and removing etc., complete as directed by Engineer-in-Charge for finished item of work. except GST.
A | Columns, Braces and Beams - Above Ground level and up to 15.0 mt level :
I | Columns, Braces and Beams | 929 | sqm | 1513.35 | 1405902.15 | 929 | 1513.35 | 1405902.15
| Authorized extra |  |  |  |  | 132.14 | 1513.35 | 199974.07 | 199974.07 |  | As Per Deviated Approved Drawing
II | Slabs (200mm Thick) | 190 | Sqm | 4491.2 | 853328 | 183.18 | 4491.2 | 822698.02 |  | 30629.984
B | Columns, Braces and Beams -from 15.0 mt level up to 18.00mt:
i | Columns, Braces and Beams | 100 | Sqm | 1649.55 | 164955 | 100 | 1649.55 | 164955
| Authorized extra |  |  |  |  | 34.76 | 1649.55 | 57338.36 | 57338.36 |  | As Per Deviated Approved Drawing
ii | Roof Top Slab (150mm Thick) | 188 | Sqm | 4895.41 | 920337.08 | 188 | 4895.41 | 920337.08
| Authorized extra |  |  |  |  | 30 | 4895.41 | 146862.3 | 146862.3 |  | As Per Deviated Approved Drawing
iii | RCC vertical walls of circular faces including both sides of wall per Sqm of member area: | 170 | Sqm | 3697.87 | 628637.9 | 170 | 3697.87 | 628637.9
| Authorized extra |  |  |  |  | 37.16 | 3697.87 | 137412.85 | 137412.85 |  | As Per Deviated Approved Drawing
6 | Providing High Yield Strength Deformed (HYSD)/ Thermo Mechanically Treated (TMT) steel bars (Fe 415 grade as per IS 1786-1979) ---- | 38 | MT | 64516.28 | 2451618.64 | 38 | 64516.28 | 2451618.64
| Authorized extra |  |  |  |  | 29 | 64516.28 | 1870972.12 | 1870972.12 |  | As Per Deviated Approved Drawing
7 | Supplying Providing and fixing in position of RCC M-30 grade ladder of 4.5 M length with 0.45 M wide steps in C C M30 grade ---- | 2 | Nos. | 4934.21 | 9868.42 | 2 | 4934.21 | 9868.42
8 | Supply and fixing H.D -20 with 560mm dia clear opening C.I. Manhole frame and cover for 914.4 mm dia chamber (20 Kg- light weight) in the roof of the Sump as shown --- | 2 | Nos. | 2799.47 | 5598.94 | 2 | 2799.47 | 5598.94
9 | Supplying, Providing and fixing in position of 6"(150mm) dia R C C (1:1.5 :3 ) prop Swan neck Ventilators with mosquito proof ---- | 8 | No. | 886.2 | 7089.6 | 0 | 0 | 0 |  | 7089.6
10 | Re filling foundation/ basement /pipe line trenches with useful excavated soils (other than black cotton soils ------ | 224 | Cum | 251.09 | 56244.16 | 224 | 251.09 | 56244.16
| Authorized extra |  |  |  |  | 430 | 251.09 | 107968.7 | 107968.7 |  | As per Excavated Quanitity
11 | Supply and delivery of DI D/F Gate Valves (Soft Seated) Resilient seated soft, sealing gate valves (Sluice valves) with body bonnet of ductile cast iron of grade ----
i | 250 mm dia. CI D/F Sluice valves | 1 | No | 53752.28 | 53752.28 | 1 | 53752.28 | 53752.28
| Authorized extra |  |  |  |  | 1 | 53752.28 | 53752.28 | 53752.28 |  | As per Site Condition
ii | 300 mm dia. CI D/F Sluice valves | 1 | No | 81238.02 | 81238.02 | 0 | 81238.02 | 0 |  | 81238.02
12 | Lowering, keeping in position and fixing C.I. sluice valves (with cap / with hand wheel & reflex valves) -----
i | 250 mm dia. CI D/F Sluice valves | 1 | No | 546.49 | 546.49 | 1 | 546.49 | 546.49
| Authorized extra |  |  |  |  | 1 | 546.49 | 546.49 | 546.49 |  | As per Site Condition
ii | 300 mm dia. CI D/F Sluice valves | 1 | No | 778.04 | 778.04 | 0 | 778.04 | 0 |  | 778.04
13 | Jointing CI pipes, fittings and valves with flanged ends including cost of jointing materials-------.
i | 250 mm dia. CI D/F Sluice valves | 1 | No | 513.77 | 513.77 | 1 | 513.77 | 513.77
| Authorized extra |  |  |  |  | 1 | 513.77 | 513.77 | 513.77 |  | As per Site Condition
ii | 300 mm dia. CI D/F Sluice valves AB | 1 | No | 579.58 | 579.58 | 0 | 579.58 | 0 |  | 579.58
14 | Constructing 904.0 mm (3’0”) dia solid block masonry inspection chamber as per IS - 4111: Part-1:1986 with cement mortar (1:6) prop using fly-ash blocks of 225 mm thick ----
i | 250 mm dia. CI D/F Sluice valves | 1 | No | 13286.14 | 13286.14 | 1 | 13286.14 | 13286.14
[6 empty] | 1 | 13286.14 | 13286.14 | 13286.14 |  | As Per Site Condition
ii | 300 mm dia. CI D/F Sluice valves | 1 | No | 13286.14 | 13286.14 | 0 | 13286.14 | 0 |  | 13286.14
15 | Providing impervious / weather proof coarse over RCC roof slabs with CM (1:3) with an average thickness of 20mm thick---- | 522 | Sqm | 422.42 | 220503.24 | 522 | 422.42 | 220503.24
| Authorized extra |  |  |  |  | 254.52 | 422.42 | 107514.34 |  |  | As Per Deviated Approved Drawing
16 | Painting to new walls with two are more coats | 780 | Sqm | 161.04 | 125611.2 | 780 | 422.42 | 329487.6
| Authorized extra |  |  |  |  | 2500 | 422.42 | 1056050 | 1056050 |  | As Per Deviated Approved Drawing including columns and stair case which was not included in estimate (including ELSR and Sump Qty)
17 | Testing of 1.0 Lakh Gallons capacity Sump/OHT for water tightness as indicated in the special conditions including cost of water ---- | 1 | Job | 79378.5 | 79378.5 | 1 | 79378.5 | 79378.5
Construction of 500 KL Capacity SUMP
1 | Earth work excavation by Mechanical means for Sump/OHT/Pump Room & Pipe Line trenches and depositing on bank in all types of soils ----- | 560 | Cum | 101.04 | 56582.4 | 560 | 101.04 | 56582.4
| Authorized extra |  |  |  |  | 227.96 | 101.04 | 23033.08 | 23033.0784 |  | As per Excavated Quanitity
2 | Plain Cement Concrete (1:3:6) Prop. nominal mix using 6 to 20 mm nominal size (SS5) well graded machine crushed hard granite metal ----- | 26 | Cum | 4787.42 | 124472.92 | 0 | 0 | 0 |  | 124472.92
3 | Providing and laying of Vibrated Reinforced Cement Concrete corresponding to M-30 grade Design Mix Concrete corresponding to IS 456 using weigh batcher with 20mm size ---
i | Bottom annular slab | 50.14 | Cum | 8785.93 | 440526.53 | 50.14 | 8785.93 | 440526.53
| Authorized extra |  |  |  |  | 54.14 | 8785.93 | 475670.25 | 475670.25 |  | As Per Deviated Approved Drawing
ii | Footings for Columns | 3 | Cum | 8785.93 | 26357.79 | 0 | 8785.93 | 0 |  | 26357.79
iii | Columns in the sump | 4 | Cum | 10721.93 | 42887.72 | 4 | 10721.93 | 42887.72
| Authorized extra |  |  |  |  | 0.18 | 10721.93 | 1929.95 | 1929.95 |  | Data Recorded in MB But not entered in Abstract
iv | Beams below roof slab | 10 | Cum | 11049.14 | 110491.4 | 5.8 | 11049.14 | 64085.01 |  | 46406.388 | Data Recorded in MB But not entered in Abstract
v | Roof Slab | 21 | Cum | 9371.95 | 196810.95 | 21 | 9371.95 | 196810.95
| Authorized extra |  |  |  |  | 1.25 | 9371.95 | 11714.94 | 11714.94 |  | As Per Deviated Approved Drawing
4 | Providing and laying of Vibrated Reinforced Cement Concrete corresponding to M-30 grade Design Mix Concrete corresponding to IS 456 using weigh batcher ----
i | Side wall | 40 | Cum | 7741.81 | 309672.4 | 36.17 | 7741.81 | 280021.27 |  | 29651.1323
5 | Centring and scaffolding charges for side wall of Sump including all materials and labour charges for forming and removing etc.---
i | Side wall | 195 | Sqm | 1207.73 | 235507.35 | 195 | 1207.73 | 235507.35
| Authorized extra |  |  |  |  | 154.23 | 1207.73 | 186268.2 | 186268.2 |  | As Per Deviated Approved Drawing
6 | Providing High Yield Strength Deformed (HYSD)/ Thermo Mechanically Treated (TMT) steel bars (Fe 415 grade as per IS 1786-1979) upto 36mm dia for RCC --- | 17 | MT | 64516.28 | 1096776.76 | 12.13 | 64516.28 | 782582.48 |  | 314194.2836
7 | Supply and fixing PVC Water bars (stopper) in position of ISI specification of 310 mm width including cost and conveyance to work site,--- | 70 | Rmt | 585.12 | 40958.4 | 70 | 585.12 | 40958.4
| Authorized extra |  |  |  |  | 277.32 | 585.12 | 162265.48 | 162265.48 |  | As Per Deviated Approved Drawing (including ELSR and Sump Qty)
8 | Providing impervious / weather proof coarse over RCC roof slabs with CM (1:3) with an average thickness of 20mm thick, premixed with water proofing compound ---- | 455 | Sqm | 422.42 | 192201.1 | 455 | 422.42 | 192201.1 |  | 0
| Authorized extra |  |  |  |  | 25.75 | 422.42 | 10877.32 |  |  | As Per Deviated Approved Drawing
9 | Re filling foundation/ basement /pipe line trenches with useful excavated soils (other than black cotton soils and other expansive soils) ----
| (Total EW Excavation-Sump Volume=912.9-785.22=127.61cum) AB | 95 | Cum | 251.09 | 23853.55 | 95 | 251.09 | 23853.55
| Authorized extra |  |  |  |  | 127.84 | 251.09 | 32099.35 | 32099.35 |  | As per Excavated Quanitity
10 | Supply and delivery of DI D/F Gate Valves (Soft Seated) Resilient seated soft, sealing gate valves (Sluice valves) with body bonnet of ductile cast iron of grade GGG-40/ SG-400/15 or GGG-50/SG-500/7 ---
i | 250 mm dia. CI D/F Sluice valves | 1 | Nos. | 53752.28 | 53752.28 | 1 | 53752.28 | 53752.28
ii | 300 mm dia. CI D/F Sluice valves AB | 1 | Nos. | 81238.02 | 81238.02 | 0 | 81238.02 | 0 |  | 81238.02
11 | Lowering, keeping in position and fixing C.I. sluice valves (with cap / with hand wheel & reflex valves) excluding cost of bolts, nuts, rubber insertion, sluice valve ----
i | 250 mm dia. CI D/F Sluice valves | 1 | Nos. | 546.49 | 546.49 | 1 | 546.49 | 546.49
ii | 300 mm dia. CI D/F Sluice valves AB | 1 | Nos. | 778.04 | 778.04 | 0 | 778.04 | 0 |  | 778.04
12 | Jointing CI pipes, fittings and valves with flanged ends including cost of jointing materials such as bolts, rubber insertion, ----
i | 250 mm dia. CI D/F Sluice valves AB | 1 | Nos. | 513.77 | 513.77 | 1 | 513.77 | 513.77
ii | 300 mm dia. CI D/F Sluice valves AB | 1 | Nos. | 579.58 | 579.58 | 0 | 579.58 | 0 |  | 579.58
13 | Constructing 904.0 mm (3’0”) dia solid block masonry inspection chamber as per IS - 4111: Part-1:1986 with cement mortar (1:6) prop using fly-ash blocks of 225 mm thick from approved source ---
i | 250 mm dia. CI D/F Sluice valves | 1 | Nos. | 13286.14 | 13286.14 | 1 | 13286.14 | 13286.14
ii | 300 mm dia. CI D/F Sluice valves | 1 | Nos. | 13286.14 | 13286.14 | 0 | 13286.14 | 0 |  | 13286.14
14 | Supply and fixing H.D -20 with 560mm dia clear opening C.I. Manhole frame and cover for 914.4 mm dia chamber (20 Kg- light weight) in the roof of the Sump | 2 | Nos. | 2799.47 | 5598.94 | 2 | 2799.47 | 5598.94
15 | Supplying, Providing and fixing in position of 6"(150mm) dia R C C (1:1.5 :3 ) prop Swan neck Ventilators with mosquito proof alluminium mesh for both ends to be provided in the roof slab of Sump --- | 6 | Nos. | 886.2 | 5317.2 | 6 | 886.2 | 5317.2
16 | Supplying Providing and fixing in position of RCC M-30 grade ladder of 5.00 M length with 0.45 M wide steps in RCC M30 grade as per the details for giving the access in to the Sump---- | 1 | No. | 5530.97 | 5530.97 | 1 | 5530.97 | 5530.97
17 | Testing of 1.0 Lakh Gallons capacity Sump/OHT for water tightness as indicated in the special conditions including cost of water required for filling to total capacity,---- | 1 | Job | 79378.5 | 79378.5 | 1 | 79378.5 | 79378.5
Providing Distribution Network System
1 | Cutting open BT road surface for laying of pipelines including stacking of excavated materials for pipeline trench work. ---- | 105 | Cum | 1183.87 | 124306.35 | 15 | 1183.87 | 17758.05 |  | 106548.3
2 | Earth work excavation by Mechanical Means upto 3 mt depth for pipe Line tranches and depositing on bank in all types of soils like morum,red earth,gravely soils,----- | 8376 | Cum | 101.04 | 846311.04 | 7500 | 101.04 | 757800 |  | 88511.04
3 | Earth work excavation by Mechanical Means upto 3 mt (Not requiring blasting) depth for pipe Line tranches and depositing on bank in all types of soils like morum----- | 523.5 | Cum | 129.14 | 67604.79 | 523.5 | 129.14 | 67604.79
4 | Earth work excavation by Manual Means upto 3 mt depth for pipe Line tranches and depositing on bank in all types of soils like morum,red earth,gravely soils,---- | 1047 | Cum | 175.77 | 184031.19 | 1047 | 175.77 | 184031.19
5 | Earth work excavation by Mechanical Means upto 3 mt depth (Blasting prohibited) for pipe Line tranches and depositing on bank in all types of soils like morum,red earth,----- | 523.5 | Cum | 652.2 | 341426.7 | 523.5 | 652.2 | 341426.7
| Authorized extra |  |  |  |  | 980 | 652.2 | 639156 | 639156 |  | As Per Site Condition
6 | Barricading, hoarding,lighting and watching etc., for water supply works for trenches of depths upto 6'-0'' "(2 Meter) --- | 138 | Rmt | 556.04 | 76733.52 | 138 | 556.04 | 76733.52
7 | Supply and filling with quarry dust in pipeline network from approved qurry as shown in the approved drawing etc----- | 260 | Cum | 299.49 | 77867.4 | 260 | 299.49 | 77867.4
8 | Supply and laying in position polythylene pipes as per IS 4984,PE100 PN6 Including cost and conveyance, of all material to work site, laying and jointing of HDPE pipes
| 110 mm dia HDPE 6Kg/Cm2 pipe AB | 9270 | Rmt | 482.86 | 4476112.2 | 7000 | 482.86 | 3380020 |  | 1096092.2
| 140mm dia HDPE 6Kg/Cm2 pipe AB | 100 | Rmt | 680.55 | 68055 | 0 | 680.55 | 0
| 225mm dia HDPE 6Kg/Cm2 pipe (pumping main+Distribution line) | 4250 | Rmt | 1690.59 | 7185007.5 | 4250 | 1690.59 | 7185007.5
| Authorized extra |  |  |  |  | 600 | 1690.59 | 1014354 | 1014354 |  | As Per Site Requirment
9 | Supply and Delivery of HDPE Fitting conforming to IS 4984-1995 Including cost and conveyance of all materials to work site.----
Bends
| 110 mm dia HDPE 6Kg/Cm2 pipe | 37 | Nos | 523.77 | 19379.49 | 0 | 523.77 | 0 |  | 19379.49
| 225mm dia HDPE 6Kg/Cm2 pipe (pumping main+Distribution line) | 12 | Nos | 4191.26 | 50295.12 | 5 | 4191.26 | 20956.3 |  | 29338.82
End caps for
| 110 mm dia HDPE 6Kg/Cm2 pipe | 62 | Nos | 153.38 | 9509.56 | 15 | 153.38 | 2300.7 |  | 7208.86
| 225mm dia HDPE 6Kg/Cm2 pipe (pumping main+Distribution line) | 4 | Nos | 694.19 | 2776.76 | 2 | 694.19 | 1388.38 |  | 1388.38
Long nech pipe ends for
| 110 mm dia HDPE 6Kg/Cm2 pipe | 62 | Nos | 268.13 | 16624.06 | 62 | 268.13 | 16624.06 |  | 0
| 225mm dia HDPE 6Kg/Cm2 pipe (pumping main+Distribution line) | 4 | Nos | 1417.92 | 5671.68 | 4 | 1417.92 | 5671.68
| Authorized extra |  |  |  |  | 16 | 1417.92 | 22686.72 | 22686.72 |  | As Per Site Requirment
MS Flanges to suit HDPE Pipes for
| 110 mm dia HDPE 6Kg/Cm2 pipe | 46 | Nos | 211.32 | 9720.72 | 46 | 211.32 | 9720.72
| Authorized extra |  |  |  |  | 16 | 211.32 | 3381.12 | 3381.12 |  | As Per Site Requirment
Tees for
| 110 mm dia HDPE 6Kg/Cm2 pipe | 46 | Nos | 511.27 | 23518.42 | 8 | 511.27 | 4090.16 |  | 19428.26
10 | Supply and delivery of DI D/F Gate Valves )Soft Seated) Resilient seated soft, sealing gate valves (Sluice Valves) with body bonnet of ductile cast iron of grade GGG-40/ SG-400/15 or GGG-50/SG-500/7 ----
| 100mm dia Sluice valves | 40 | Nos | 14833.23 | 593329.2 | 20 | 14833.23 | 296664.6 |  | 296664.6
| 250mm dia Sluice Valves AB | 8 | Nos | 53752.28 | 430018.24 | 7 | 53752.28 | 376265.96 |  | 53752.28
11 | Lowering, keeping in position and fixing C.I Sluice valves (with cap/ with hand wheel & reflex valves) excluding cost of bolts,nuts,rubber insertion,sluice valve ----
| 100mm dia Sluice valves | 40 | Nos | 137.53 | 5501.2 | 20 | 137.53 | 2750.6 |  | 2750.6
| 250mm dia Sluice Valves AB | 8 | Nos | 546.49 | 4371.92 | 7 | 546.49 | 3825.43 |  | 546.49
12 | Constructing 904.0mm (3'0'')dia solid block masonry inspection chamber as per IS -4111:PART-I:1986 with cement mortar (1:6) prop using fly-ash blocks of 225mm thick from approved source having a minimum crushing strength of 10N/sq.mm ----- | 48 | Nos | 13286.14 | 637734.72 | 0 | 13286.14 | 0 |  | 637734.72
13 | Maunfacture & supply and delevary of CI Dismantaling joints
i | 100mm dia PN 16 Class | 40 | Nos | 7892.83 | 315713.2 | 0 | 7892.83 | 0 |  | 315713.2
ii | 250mm dia PN 16 Class | 8 | Nos | 18794.19 | 150353.52 | 0 | 18794.19 | 0 |  | 150353.52
14 | Jointing CI Pipes,fittings and valves with flanged ends including cost of jointing materials such as bolts,rubber insertion,white lead including filling with water,with lead upto 500meter-----
| 100mm Dia PN.16 CLASS | 160 | Nos | 219.63 | 35140.8 | 60 | 219.63 | 13177.8 |  | 21963
| 250mm dia PN,16 CLASS AB | 32 | Nos | 577.35 | 18475.2 | 32 | 577.35 | 18475.2
| Authorized extra |  |  |  |  | 16 | 577.35 | 9237.6 | 9237.6 |  | As Per Site Requirment
15 | Manifacture,Supply and delivery of Single Chmaber DI Air Valve with body and cover in Ductile iron of Grade GGG-40/ SG-400/15 or GGG-50/SG-500/7 or equivalent grade as per I.S.3896-Part2-1985 ------ | 17 | Nos | 36677.48 | 623517.16 | 16 | 36677.48 | 586839.68 |  | 36677.48
16 | Labour charges for fixing Kinetic Air Valves with isolating Sluice valves, Double Air Valves/Air cushion valve excluding cost of jointing material such as bolts,nuts,and rubber insertions, ----- | 17 | Nos | 227.23 | 3862.91 | 16 | 227.23 | 3635.68 |  | 227.23
17 | Constructing 904.0mm (3'0'')dia solid block masonry inspection chamber as per IS -4111:PART-I:1986 with cement mortar (1:6) prop using fly-ash blocks of 225mm thick from approved source having a minimum crushing strength of 10N/sq.mm including plastering with cement mortor 1:3 prop----- | 17 | Nos | 8337.07 | 141730.19 | 0 | 8337.07 | 0 |  | 141730.19
[5 empty] | 29474654.41 |  |  | 32926512.37 | 7623607.5384 | 4425962.6553
| Deduct Tender Primium 16.01% |  |  |  | 4718892.11 |  |  | 5271534.6304
|  |  | Checking |  | 24755761.89 |  |  | 27654977.7396
Supplimentary Item
SUP NO | Supplimentary items for ELSR 500KL
1 | Supply and delivery of DI D/F Gate Valves (Soft Seated) Resilient seated soft, sealing gate valves (Sluice valves) with body bonnet of ductile cast iron of grade GGG-40/ SG-400/15 or GGG-50/SG-500/7 or equivalent grade as per I.S.3896-part2-1985 and subsequent revisions, wedge fully rubber lined with EPDM food grade quality and seals of NBR and the valves should be of vacuum tight and 100% leak proof with face to face dimensions as per BS5163-89/IS14846-2000/DIN 3202 F 4. All the valves should be with Electrostatic powder coating both inside and outside pocket less body passage. Drilled as per requirement of the department including cost and conveyance of material to work site, as directed by Engineer-in-Charge for finished item of work, except GST.
i | A)80mm Dia Scour valve for Pipeline |  |  |  | 1No | 2 | 9444.5221 | 18889.04 |  |  | As per Site Requirment
ii | B)150mm Dia Gate valve for OHT Scour |  |  |  | 1No | 1 | 19615.4689 | 19615.47 |  |  | As per Site Requirment
iii | C)400mm Dia Gate valve for Sump Scour |  |  |  | 1No | 1 | 216673.9302 | 216673.93 |  |  | As per Site Requirment
2 | Lowering, keeping in position and fixing C.I. sluice valves (with cap / with hand wheel & reflex valves) excluding cost of bolts, nuts, rubber insertion, sluice valve and tail pieces,as directed by Engineer-in-Charge etc., complete for finished item of work, except GST.
i | A)80mm Dia Scour valve for Pipeline |  |  |  | 1No | 2 | 86.9876 | 173.98 |  |  | As per Site Requirment
ii | B)150mm Dia Gate valve for OHT Scour |  |  |  | 1No | 1 | 195.7774 | 195.78 |  |  | As per Site Requirment
iii | C)400mm Dia Gate valve for Sump Scour |  |  |  | 1No | 1 | 653.4741 | 653.47 |  |  | As per Site Requirment
3 | Jointing CI pipes, fittings and valves with flanged ends including cost of jointing materials such as bolts, rubber insertion, white lead including filling with water, with lead up to 500 meters and testing to required pressure complete. (Reference to specifications. BIS No.3114/1994.), as directed by Engineer-in-Charge for finished item of wor, except GST.
i | A)80mm Dia Scour valve for Pipeline |  |  |  | 1No | 2 | 119.7421 | 239.48 |  |  | As per Site Requirment
ii | B)150mm Dia Gate valve for OHT Scour |  |  |  | 1No | 1 | 278.0482 | 278.05 |  |  | As per Site Requirment
iii | C)400mm Dia Gate valve for Sump Scour |  |  |  | 1No | 1 | 486.7853 | 486.79 |  |  | As per Site Requirment
4 | Centrifugally cast (spun) Ductile Iron pressure pies with flanged (welded) ends for water,gas,sewage conforming to IS: 8329/2000 in standard working lengths of 1,2,3,4,5 mts for classification K9 with cement mortar lining inside the pipes with outside zone coating Rates are ex-factory,excluding transportation & taxes | [7 empty] | SSR 18-19
A | For 500KL ELSR | [9 empty] | As per Site Requirment
i | A)250mm DIA D/F Flanged Pipes (1Mtr Length) For Inlet |  |  |  | 1No | 4 | 8427.5277 | 33710.11
ii | B)250mm DIA D/F Flanged Pipes (2Mtr Length) For Inlet |  |  |  | 1No | 9 | 11316.1928 | 101845.73
i | C)250mm DIA D/F Flanged Pipes (1Mtr Length) For Outlet |  |  |  | 1No | 4 | 8427.5277 | 33710.11
ii | D)250mm DIA D/F Flanged Pipes (2Mtr Length) For Outlet |  |  |  | 1No | 9 | 11316.1928 | 101845.73
i | E)250mm DIA D/F Flanged Pipes (1Mtr Length) For Over flow |  |  |  | 1No | 5 | 8427.5277 | 42137.64 |  |  |  | 58.27
ii | F)250mm DIA D/F Flanged Pipes (2Mtr Length) For Over Flow |  |  |  | 1No | 9 | 11316.1928 | 101845.73 |  |  |  | 29.02
iv | G)150mm DIA D/F Flanged Pipes (1Mtr Length) For Scour |  |  |  | 1No | 5 | 4854.5204 | 24272.6
v | H)150mm DIA D/F Flanged Pipes (2Mtr Length) For Scour |  |  |  | 1No | 8 | 6437.6252 | 51501
B | For 500KL Sump | [9 empty] | As per Site Requirment
i | A)250mm DIA D/F Flanged Pipes (1Mtr Length) For Inlet |  |  |  | 1No | 4 | 8427.5277 | 33710.11
ii | B)250mm DIA D/F Flanged Pipes (2Mtr Length) For Inlet |  |  |  | 1No | 3 | 11316.1928 | 33948.58
ii | C)250mm DIA D/F Flanged Pipes (2Mtr Length) For Outlet |  |  |  | 1No | 2 | 11316.1928 | 22632.39
iii | D)250mm DIA D/F Flanged Pipes (4Mtr Length) For Outlet |  |  |  | 1No | 4 | 16190.7525 | 64763.01
5 | Centrifugally cast (span) Ductile Iron Fittings conforming to IS:9523/2000 having dimensions as per table. The rates mentioned here under are for fitting,zinc coated externally with inside mortor lining (with finishing as per class 13/IS 9523/2000) (ex-works) Excluding Tranportation and Taxes
i | Special For 500KL ELSR (Duck foot bend,Bell-mouth,Tail piece,bends) |  |  |  | 1KG | 520 | 105.2063 | 54707.29 |  |  | As per Site Requirment
i | Special For 500KL Sump (Duck foot bend,Bell-mouth,Tail piece,bends) |  |  |  | 1KG | 487 | 105.2063 | 51235.48 |  |  | As per Site Requirment
6 | Providing and laying of Vibrated Reinforced Cement Concrete corresponding to M-30 grade Design Mix Concrete corresponding to IS 456 using weigh batcher with 20mm size well graded machine crushed hard granite chips (Coarse aggregate) from approved quarry with a minimum cement content of 400 kg/CuM including cost and conveyance of all materials like cement, Coarse aggregate, Fine aggregate, water etc., to site, including centering & shuttering using steel scaffolding pipes, jack props, wallers, foot plates, brackets, steel centering plates weigh batcher etc machine mixing, laying concrete, vibrating, finishing smooth to required levels, curing, pumping to work spot, lifting of material with mechanical equipment like winch, etc., all other incidental and operational charges, all labour charges, etc., but excluding cost of steel and its fabrication charges etc., complete as directed by Engineer-in-Charge for the following finished items of work, excluding GST & seigniorage charges.
i | RCC SLAB For Sluice Valve Chambers for ELSR |  |  |  | 1Cum | 1 | 7000.6137 | 7000.61 |  |  | As per Site Requirment
ii | RCC SLAB For Sluice Valve Chambers for Sump |  |  |  | 1Cum | 1 | 7000.6137 | 7000.61 |  |  | As per Site Requirment
iii | Pedestals Concrete |  |  |  | 1Cum | 3 | 7000.6137 | 21001.84 |  |  | As per Site Requirment
7 | Supply and Fixing water level indicater containing indicater with suitable probe height with chain pully arrengement and using 15m standard cable as per site reserviour with 250mm dia ball and 40mm squre pipe frame conforming to IS 1230 Drilling hole in roof slab including all accessories etc., complete as directed by the department officers, excluding GST
i | For 500KL ELSR |  |  |  | 1 JOB | 1 | 27339.1649 | 27339.16 |  |  | As per Site Requirment
ii | For 500KL GLSR |  |  |  | 1 JOB | 1 | 27339.1649 | 27339.16 |  |  | As per Site Requirment
8 | Manifacturing,supply,delivery and fixing at site, the lightening protective system with copper plates and connecters with protective coating,including suitable earthing arrengements as per the standard specifications including cost and conveyance, labour charges etc.,complete as directed by the departmental officers, except GST
i | For 500KL ELSR |  |  |  | 1No | 1 | 25932.3325 | 25932.33 |  |  | As per Site Requirment
ii | For 500KL GLSR |  |  |  | 1No | 1 | 24922.7726 | 24922.77 |  |  | As per Site Requirment
9 | Supply and Fixing of SS Railing containing vertical size 40mm thickness 16 gauge at height 1.10M and top horizental pipes 40mm size and thickness 16 gauge and middle 25mm size thickness 16 gauge and including base covers and L Bends and Dummys as per standard requirements including cost and conveyance of all labour charges etc., complete, except GST
i | For 500KL ELSR |  |  |  | 1Rmt | 100 | 2774.8196 | 277481.96 |  |  | As per Site Requirment
ii | For 500KL Sump |  |  |  | 1Rmt | 45 | 2774.8196 | 124866.88 |  |  | As per Site Requirment
iii | For Staircase |  |  |  | 1Rmt | 135 | 2774.8196 | 374600.65 |  |  | As per Site Requirment
Supplimentary items for Sump 500KL
10 | Manfacturing supply delivery lowering laying jointing testing of MS pipe using 8mm thick MS piate including cost and conveyanc of all material and cost oe epoxy painting labour charges and all incidental operation charges complete
i | A)150mm Dia MS Pipe |  |  |  | 1Rmt | 30 | 2245.4036 | 67362.11 |  |  | As per Site Requirment
ii | B)250mm Dia MS Pipe |  |  |  | 1Rmt | 5 | 3506.8775 | 17534.39 |  |  | As per Site Requirment
11 | Manfacturing supply delivery lowering laying jointing testing of MS pipe using 8mm thick MS piate including cost and conveyanc of all material and cost oe epoxy painting labour charges and all incidental operation charges complete
i | A)400mm Dia MS Pipe |  |  |  | 1Rmt | 15 | 5992.321 | 89884.81 |  |  | As per Site Requirment
12 | Manufacture, Supply, & Delivery of HDPE fittings conforming to IS 4984 - 1995 including transportation to anywhere in T.G. Excluding taxes
A) MS Flanges
i | 150mm Dia |  |  |  | 1No | 2 | 1515.3528 | 3030.71 |  |  | As per Site Requirment
ii | 250mm Dia |  |  |  | 1No | 1 | 2463.8797 | 2463.88 |  |  | As per Site Requirment
iii | 400mm Dia |  |  |  | 1No | 3 | 5078.5312 | 15235.59 |  |  | As per Site Requirment
13 | Manifacture, Supply and Delivery of R.C.C Spun / Vibrated cast (Reinforced) Socket and Spigot pipes conforming to B.I.S. 458/2003, Cost of Rubber Ring,transportation charges and Including Labour Charges for lowering ,laying,jointing in readymade trenches true to alighenment and Gradient and all incidental operation charges etc complete |  |  |  | 1Rmt | 30 | 801.4575 | 24043.72
Supplimentary items for Pipeline Distribution Network System
14 | Supply and Fixing of pre-cast RCC Chamber bottom size width 36' Dia and top 21' Dia over CC Bed (1:4:8) including cast and conveyance all material labour charges and incidental charges etc complete
| For Sluice valves |  |  |  | 1No | 30 | 4073.515 | 122205.45 |  |  | As per Site Requirment
15 | Supply and fixing M.D -10 with 560mm dia clear opening C.I. Manhole frame and cover for 914.4 mm dia chamber (20 Kg- light weight) in the roof of the Sump as shown in the detail drawing with a clear opening of 760 mm dia including cost and conveyance of all materials to site, all labour charges, complete as directed by Engineer-in-Charge for finished item work, except GST.
| for Sluice valve |  |  |  | 1No | 30 | 1496.7018 | 44901.05 |  |  | As per Site Requirment
16 | Re filling foundation/ basement /pipe line trenches with useful excavated soils (other than black cotton soils and other expansive soils) with initial lead and lifts spreading in layers not exceeding 150mm thick, consolidating each deposited layer by watering and ramming, compacting by earth mover to achieve optimum moiture content including cost and conveyance of water to work site and all operational, incidental, all labour charges, hire charges of T&P etc., complete for finished item of work, as directed by Engineer-in-charge (APSS No. 309 & 310), except GST. (Total Excavation-Deduct Raft Foundation Qtys=768.46-128.65=639.81) |  |  |  | 1Cum | 8925 | 20.9958 | 187387.4 |  |  | As per Site Condition
17 | Centrifugally cast (span) Ductile Iron Fittings conforming to IS:9523/2000 having dimensions as per table. The rates mentioned here under are for fitting,zinc coated externally with inside mortor lining (with finishing as per class 13/IS 9523/2000) (ex-works) Excluding Tranportation and Taxes
| Specials |  |  |  | 1KG | 1050 | 105.2063 | 110466.64 |  |  | As per Site Condition
18 | Manifacturing supply delivery of Air valve gauge fabrication of size 1x1x1m using 50x50x6mm MS angles vertical and horizental frame and fixing 10mm squre rods c/c 150mm including cost and convenyance of all material and cost epioxy paint labour charges and fixing gauge in cement concrete morter and allincidental operation etc complete. |  |  |  | 1 No | 17 | 11728.2695 | 199380.58
19 | Plain Cement concrete (M 20) grade using 20mm and 10mm metal using concrete mixer nominal size well graded machine crushed granite stone chips from approved quarry including cost and conveyance and seigniorage charges of all materials like cement, sand coarse aggregate, water etc., to site, cost of seigniorage on materials including centering, shuttering machine mixing, laying concrete, tamping finishing smooth to required levels, curing mall other incidental and operational charges, labour charges etc., complete but excluding cost of steel and its fabrication charges for the following finished item of work.
i | CC Road Concrete for Pipeline restoring of roads |  |  |  | 1Cum | 30 | 4451.7342 | 133552.026 |  |  | As per Site Condition
20 | Manufacture, Supply, & Delivery of HDPE fittings conforming to IS 4984 - 1995 including transportation to anywhere in T.G. Excluding taxes
i | MS Flanges to suit HDPE Pipes for | [9 empty] | As per Site Condition
| 225 mm dia HDPE 6Kg/Cm2 pipe |  |  |  | 1No's | 20 | 792.9837 | 15859.67
ii | Tees for
| 225 mm dia HDPE 6Kg/Cm2 pipe |  |  |  | 1No's | 9 | 4069.8864 | 81397.73 |  |  | As per Site Condition
D) Construction Of Panal Board Room
21 | Earth work excavation by Manual Means upto 3 mt depth for pipe Line tranches and depositing on bank in all types of soils like morum,red earth,gravely soils,ordinary soils upto SDR in all condition including hire and operational charges of mechinery,labour charges for setting out,construction of shoring and bracing removal of stumps and all other deletarious material,dressing on sides & bottom of trench in all conditions viz dry,wet and slushy etc.,as directed by Engineer-in-charge etc.,complete for finished item of work as per SS20 B (APSS 308),except GST |  |  |  | 1Cum | 98.0133 | 84.8625 | 8317.65 |  |  | As Per Deviated Approved Drawing
22 | Earthwork Excavation by mechanical means upto 3m depth (Blasting prohited) for OHT Trenches in Hardrock including hire and operational charges of mechinary labour charges for setting out construction of shoring and bracing removal stumps and deldtarious material,etc complete |  |  |  | 1Cum | 29.2767 | 547.7828 | 16037.27 |  |  | As Per Deviated Approved Drawing
23 | Plain Cement Concrete (1:4:8) prop.using 40mm nominal size well graded hard broken granite metal from approved quarry including cost and conveyance of all material, all labour charges for machine mixing of concrete, laying concrete, compacting by vibration including curing, finishing top surface to required levels neatly etc., complete as derected by Engineer-in-charge for finished item of work in foundations, excluding GST & seigniorage charges. |  |  |  | 1Cum | 12.54 | 3478.938 | 43625.88 |  |  | As Per Deviated Approved Drawing
24 | Providing and laying of Vibrated Reinforced Cement Concrete corresponding to M-30 grade Design Mix Concrete corresponding to IS 456 using weigh batcher with 20mm size ----
| A)Footing,Column,Beams,Roof Slab |  |  |  | 1Cum | 15.2925 | 7000.6137 | 107056.88 |  |  | As Per Deviated Approved Drawing
25 | Centering and scaffolding charges for RCC members including all materials and labour charges for forming and removing etc., complete as directed by Engineer-in-Charge for finished item of work. except GST.
| A) Above Ground Level Columns and Beams, Roof Slab |  |  |  | 1Sqm | 116.42 | 1271.0642 | 147977.29 |  |  | As Per Deviated Approved Drawing
26 | Providing High Yield Strength Deformed (HYSD)/ Thermo Mechanically Treated (TMT) steel bars (Fe 415 grade as per IS 1786-1979) upto 36mm dia for RCC and RCM works including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and size and tying and lap-splicing with binding wire of 18 SWG, forming grills for reinforcement work as per approved designs and drawings including cost and conveyance of steel bars including all wastages such as overlaps, couplings, chairs, spacer bars including cost and conveyance of binding wire, cover blocks and all incidental, operational, all labour charges such as cutting, bending, placing in position, tying etc., complete for finished item of work, as directed by Engineer-in-Charge (APSS No.126), excluding GST and seignorage charges. |  |  |  | 1MT | 3 | 54187.2217 | 162561.67 |  |  | As Per Deviated Approved Drawing
27 | Re filling foundation/ basement /pipe line trenches with useful excavated soils (other than black cotton soils and other expansive soils) ---- |  |  |  | 1Cum | 121.67 | 210.8898 | 25658.96 |  |  | As Per Deviated Approved Drawing
28 | RR Masonary in CM (1:6) 2nd sort stones including cost and conveyance of all material labour charges and all incidental and operational charges etc compiete |  |  |  | 1Cum | 15 | 4142 | 62130 |  |  | As Per Deviated Approved Drawing
29 | Providing Brick Masonry work in CM(1:6) prop with flyash cement solid blocks of size 290x225x140 mm and compresive strength not less than 50Kg/sqm including cost and conveyance of all materials, labour charges, seigniorage charges, scaffolding and curing, etc., excluding GST, complete for wall. |  |  |  | 1Cum | 30 | 4692.0174 | 140760.52 |  |  | As Per Deviated Approved Drawing
30 | Supply & fixing of Rolling shutter made of 80x1.25 mm machine rolled CRCA laths, interlocked together through their entire length and jointed together at the ends by end-locks, mounted on specially designed pipe shaft of 50mm Diameter nominal bore MS B class pipe with brackets, plates, guide channels, stoppers, bottom locking plates andarrangements for inside & outside locking with push-pull operations including cost of hood cover and springs complete, painted with one coat of approved steel primer, locks, ball bearings, all accessories etc complete for finisheditemofworkasperspecialSpec:110, Excluding GST |  |  |  | 1Sqm | 8.06 | 3897.6439 | 31415.0096 |  |  | As Per Deviated Approved Drawing
31 | Plastering with 12mm thick in single coat in CM (1:3) finished smooth including cost and conveyance of all materials to site, finishing, curing, scaffolding and all operational, incidental, labour charges etc., including cutting grooves where ever necessary etc., complete for finished item of work as directed by Engineer-in-Charge, excluding GST (As per SS 903). |  |  |  | 1Sqm | 314.33 | 318.0523 | 99973.39 |  |  | As Per Deviated Approved Drawing
32 | BLD-CSTN-13-16 - Supply and fixing Teak Wood framed FLUSH Doors single shutter door with flush shutter as per approved drawings with best quality 2nd class teakwood frame od size 115x65mm and flush door shutters of 30 mm thick solid bond wood block board typer with teak veneer on one face and commercial ply on another face (One side Teak) teak wood internal lipping as per drawing including fixing of 6 Nos. MS Z hold fasts of size 300 x 40 x 5mm size including cost of Powder Coated/ Chromium Plated Mild Steel fixtures of 3 Nos. butt hinges 150 x 31.75 x 3.5 mm, 2 No tower bolt of 250x12mm dia, 1 No.CP Aldrops - 300 mm long and 2 Nos. CP handles of 150 mm size & 1 No. 63 mm long door stopper including fixing the fixtures to door with required no. of brass screws, bolts and nuts including labour charges for fixing the frame in position, fixing the shutter to the frame etc., complete for finished item of work as per APSS 1001 & 1002 (0.90x2.15) |  |  |  | 1Sqm | 10.7 | 4431.2597 | 47414.48 |  |  | As Per Deviated Approved Drawing
33 | Ceramic wall tiles supply of glazed red or white fully body ceramic wall tilws of size 200 x 300 mm /245 mm x 325 mm and thickness 6mm 1st quality, set over CSTN-9- over a base coat of cement mortar (1:8) prop., 12 mm thick and filling the joints with 3mm Nylon spacers at each corner of the tile and joints grooted with laticrete epoxy grout of pigment of approved shade of tiles over a wall. or R.C.C. slab, including cost and conveyance of all materials like cement, sand, water, tiles, white cement etc., to site (excluding cost of C.C. bed) cost of excluding seigniorage on all materials cost of base coat and all labour charges for mixing of cement mortar, laying tiles to required slope as directed by the Ebgineer-in-charge curing etc., complete for finished item of work, IS 13711, IS:13712 IS 13713 |  |  |  | 1Sqm | 15.75 | 713.8803 | 11243.61 |  |  | As Per Deviated Approved Drawing
34 | Painting to new walls with 2coat of Red mixed oil bound washable distemper approved brand and shade over a base coat of appropiated primer of approved brand making 3 coats in all to give even shade after thourughly brushing the surface to remove all duct and remains of loose poweredf material including cost and conveyance of all materials to work site and all operation incidental labour charges etc compiete for finished item of work complete as per SS911 For internal walls |  |  |  | 1Sqm | 314.33 | 135.2557 | 42514.93 |  |  | As Per Deviated Approved Drawing
35 | Providing imperious / weather proof coarse over RCC roof slabs with CM (1:3) with an average thickness of 20mm thick premixed with water proofing compound like ACCO proof or any other ISI make at one KG per bag of cement as prescribed by the manufacturer and laid over the proof slab to required slopes as directed by the engineer in charge when slab is in green including cost and conveyance of all material to site all labour charges and for all operation maintaining necessary slope finishing smooth and lining curing etc complete |  |  |  | 1Sqm | 85 | 354.7906 | 30157.2 |  |  | As Per Deviated Approved Drawing
36 | Supplying and fixing of Unplasticised Poly Vinyl Chloride (UPVC) sliding windows two track sliding duly manufactured using UPVC reinforced profiles of (62 mm x 60 mm)/(60 mm x 45 mm) / (60 mm x 52 mm) x 2.0 mm for outer frames, (66 mm x 38 mm) / (58 mm) x 39 mm)/ (60 mm x 42 mm) x 2.0 mm for sliding shutter frames capable of mounting single glazing system, structurally reinforced with hot dip galvanized up to 50 micros of minimum thickness of 1.2 mm prefabricated & welded through fusion welding the window sash shall be fitted with 5 mm thick clear float glass of reputed make duly fixed with TPV Gaskets/EPDM weathering seal resistant accessories like locking system 1 No., per set of sashes and the system is to be installed at the site using anchor fasteners, silicon rubber sealent, easy glazing/ deglazing at site etc., including cost and conveyance of all materials, accessories, labour charges for transportation, erection at site with templates for casement sizing complete for finished item of work. |  |  |  | 1Sqm | 10.8 | 6083.359 | 65700.2767 |  |  | As Per Deviated Approved Drawing
SANITARY ITEMS
37 | Supplying laying jointing and testing 101.6mm SWG SP-1 pipes of ISI Make confirming to ISI 651 & 4127 with airtight cement joints in CM 1:5:1 prop. Including excavation of trenches and socket pits in any soil(except rock requiring blasting) upto 914.4 mm(3"0') depth and refilling with watering and tamping |  |  |  | 1Rmt | 40 | 403.6475 | 16145.9 |  |  | As per Site Requirment
38 | Supplying and fixing 150 mm x 100 mm SWG gully traps confirming to ISI 651 & 4127 with C.I. grating & Cost brick masonry in CM 1:6 prop.. Intermediate chamber and fitted with 304.8mm x 288.6mm (12"x9") C.I. Frme and hinged cover. |  |  |  | 1No | 1 | 590.6849 | 590.68 |  |  | As per Site Requirment
39 | Constructing 904.0mm (3"0') dia solid brick masonry inspection chamber as per IS - 4111: Part-1: 1986 with cement mortar (1:6) prop. Using 2nd class clay bricks of 225mm thick from approved source having a minimum crushing strength of 5 N/ Sq.mm including plastering with cement mortar 1:3 prop; 1/2" thick both inside and outside fitted with 20" dia RCC Manhole covers and frames including excavating pits upto a depth of 904mm (3'-0") in all sorts of soils ( excluding rock) and laying cement concrete (1:4:8) 150mm thick using 40mm HBG Metal and PCC 1:2:4 benching and channel 100 mm thick as per standard specification and including cosrt and conveyance of all materials like cement,sand , bricks, water etc.m, to site, cost of seigniorage charges on all materials and all incidentall and operational, labour charges like mixing cement mortar , constructing masonry, lift charges curing, etc., complete for finished item of work as per standard specification. |  |  |  | 1No | 3 | 6986.0782 | 20958.23 |  |  | As per Site Requirment
40 | Supply and fixing of approved make Orissa pan white glaze W.C. ist quality ISI Marked confirming to IS:2556 -Part-3-2004 with "P" or "S" Trap : 580mm x 440mm duly provading construction brick masonry and CC squatting plate including cost and conyence of all materials and labour charges etc complete as per standard practice for finished item. |  |  |  | 1No | 1 | 1504.8572 | 1504.86 |  |  | As per Site Requirment
41 | Supplying and fixing low down porcelain flushing tank with lid 10Lit capacity with internal components |  |  |  | 1No | 1 | 2418.0755 | 2418.08 |  |  | As per Site Requirment
42 | Supplying and fixing Indian make Flat Back Wash Hand Basin 1st quality confirming to IS: 2556-Part-4:1972 with waste fittings like rubber plug , chain, 32mm nominal size C.P. Fitting with parallel pipe thread confirming to IS: 2963-1979 and fitted with 15mm nominal bore Chromium Plated Pillar Tap og 1st quality Indian make 400 grams complete with standard CI Brackets including wooden block : 630x 450mm - Single C.P. Pillar cock |  |  |  | 1No | 8 | 1890.3713 | 15122.97 |  |  | As per Site Requirment
43 | Supply and fixing of 90mm dia single socket PVC/SWR Pipe- 4kg/sqm including cost and conveyance of all material labour charges etc., |  |  |  | 1Rmt | 15 | 128.8239 | 1932.36 |  |  | As per Site Requirment
44 | Supply of rubber lubricant 500 grams UPVC/SWR Pipe fittings |  |  |  | 1No | 1 | 111.6479 | 111.65 |  |  | As per Site Requirment
45 | S&F 20 mm Nominal Bore GI Pipe Medium grade properties & weight as per IS 1239 ISI Markwith GI Fittings including the cost of pipe and its fittings & labour charges complete |  |  |  | 1Rmt | 10 | 194.6636 | 1946.64 |  |  | As per Site Requirment
46 | S&F 25 mm Nominal Bore GI Pipe Medium grade properties & weight as per IS 1239 ISI Markwith GI Fittings including the cost of pipe and its fittings & labour charges complete |  |  |  | 1Rmt | 30 | 255.7412 | 7672.23 |  |  | As per Site Requirment
47 | S&F of 15mm brass body CP finish bib tap of not less than 300 grams weight with quarter turn spindle with either internal or external threaded connection confirming to IS 8931 |  |  |  | 1No | 1 | 518.1595 | 518.16 |  |  | As per Site Requirment
48 | S&F of 15mm brass body CP finish pillar tap of not less than 300 grams weight screw type(full turn) confirming to IS 8931 |  |  |  | 1No | 1 | 542.0127 | 542.01 |  |  | As per Site Requirment
49 | S&F of 15mm brass angle stop valve of qurter turn spindle type of not less than 400 grams weight with internal threaded connection confirming to IS 8931 |  |  |  | 1No | 1 | 525.7942 | 525.79 |  |  | As per Site Requirment
50 | Supplying and fixing of 15mm nom,inal size PVC Connection with brass union nut C.P. Coated |  |  |  | 1No | 2 | 90.654 | 181.31 |  |  | As per Site Requirment
51 | Providing & Placing on terrace ( at all floor levels) polyethylene water storage tank with Double layer approved brand & manufacture with cover and suitable locking arrangement & making necessary holes for inlet & outlets and overflow pipes but without fittings & base support for tanks |  |  |  | 1Ltr | 500 | 6.6772 | 3338.6 |  |  | As per Site Requirment
52 | Supplying & Fixing white glazed flat back half stall urinals 1st quality conforming to IS:2556-1995 with standard C.P. Spreader fixed with screws complete Indian make : 590 x 375 x 390 mm |  |  |  | 1No | 4 | 2438.1148 | 9752.46 |  |  | As per Site Requirment
Cost and Erection of Pumps and Motors With Electrical Panal Board
53 | Supply, delivery and fixing of 20 HP 3 phase 415 Volts submersible monoblock horizontle booster pump set with a Head of 25 Mts. to discharge 37LPS of Lubi/texmo including cost and conveyance of all materials and labor charges etc complete as directed by the TSSC Engineers. |  |  |  | 1No | 2 | 104204.3604 | 208408.72 |  |  | As per Site Requirment
54 | Supply, delivery and laying of 4 core, 4 sq mm, Copper armored underground cable finotex make from outdoor panel to pump set near MS shell including necessary connection with cost and conveyance of taxes duties with all other incidental and operational charges etc. complete as directed by the TSSC Engineers. |  |  |  | 1Rmt | 26 | 166.9942 | 4341.85 |  |  | As per Site Requirment
55 | Supply fabrication of suitable outdoor panel with enamel coated in 16 SWG iron sheet comprising of below items internal wiring with necessary locking arrangements as mentioned below for 1 No. 20 HP open well submersible pump set of L&T/BCH of its equivalent make a) 32 Amps contactors 3 No. b) Suitable relay 1 No.c) Suitable Timer 1 No d) 100 amps MVVB of 35 KVA 1 No e)32 amps MCB for capacitor 1 No f) 0-500 Volts voltmeter Digital 1 No. g) 0-60 amps Ammeter Digital 1 No h) Capacitor 15 KV. AR 1 No. i) RYB indication lamps 1 set etc., complete as directed by the TSSC Engineers. |  |  |  | 1Set | 2 | 56110.0402 | 112220.08 |  |  | As per Site Requirment
56 | Supply, Transportation and Installation of 150mmx50mmx1.6mm thick hot dip GI perforated cable tray without cover along with coupler plates, Anchor bolts and nuts etc complete and the tray should be fitted on the wall / Ceiling etc. complete for finished item of work. |  |  |  | 1Rmt | 30 | 403.7919 | 12113.76 |  |  | As per Site Requirment
57 | Supply and fixing air vessel made of 250 mm dia, 8 mm thick MS sheet, 1200mm in height with air release valve on top and flanged connection to riser, drain arrangement with 25mm dia Gun metal wheel valve, with required accessories, pressure gauge and painting with synthetic enamel paint of approved shade as required. |  |  |  | 1No | 1 | 14250.9483 | 14250.95 |  |  | As per Site Requirment
58 | Manufacture, Supply and delivery of 150 Dia DI D/F Gate Valves (Soft Seated) Resilient seated soft sealing gate valves (Sluice valves) with body bonnet of ductile cast iron of grade GGG-40/ SG- 400/15 or GGG-50/SG-500/7 or equivalent grade as per I.S.3896-part2-1985 and subsequent revisions, wedge fully rubber lined with EPDM food grade quality and seals of NBR and the valves should be of vacuum tight and 100% leak proof with face to face dimensions as per BS5163-89/IS14846-2000/DIN 3202 F 4. All the valves should be with Electrostatic powder coating both inside and outside pocket less body passage. Drilled as per requirement of the dept |  |  |  | 1No | 2 | 19615.4689 | 39230.94 |  |  | As per Site Requirment
59 | Supply and delivery of 150mm dia CI D/F Non return valve heavy duty round body conforming IS 5312/part 1/1984, including all taxes duties etc., complete the valves shall be tested requirement ISI make labor charges etc complete as directed by the TSSC Engineers. |  |  |  | 1No | 2 | 22828.7707 | 45657.54 |  |  | As per Site Requirment
4603294.0123
Grand total |  | 32258271.7519
As Per Execution |  | 32258271.7519
As Per Agreement |  | 24755761.89
Difference in Agreement and Execution |  | 7502509.8619
Estimate Amount |  | 39500000
Project Engineer |  |  | Dy Zonal manager(E) |  |  |  | Zonal manager
TSIIC Ltd, Shamshabad Zone |  |  | TSIIC Ltd, Shamshabad Zone |  |  |  | TSIIC Ltd, Shamshabad Zone

## Supplimentary Data Details
Providing water supply fecilities to Electronic Hardware Manufactering Cluster At Maheshwaram (V&M) R R Dist
Supplimentary Item Data
500KL ELSR and Sump Data
1 | Manufacture, Supply and delivery of DI D/F Gate Valves (Soft Seated) Resilient seated soft sealing gate valves (Sluice valves) with body bonnet of ductile cast iron of grade GGG-40/ SG- 400/15 or GGG-50/SG-500/7 or equivalent grade as per I.S.3896-part2-1985 and subsequent revisions, wedge fully rubber lined with EPDM food grade quality and seals of NBR and the valves should be of vacuum tight and 100% leak proof with face to face dimensions as per BS5163-89/IS14846-2000/DIN 3202 F 4. All the valves should be with Electrostatic powder coating both inside and outside pocket less body passage. Drilled as per requirement of the dept
i | A) 80MM Dia Gate Valve PN-16
| Basic Rate (as per CSSR-(PH 27-2)-2018-19) | 1 | No | 9426 | 1No | 9426 | (PH-27 S o R-2)
| Add 5% Transportation charges on Basic |  |  |  |  | 471.3
9897.3
| Add 13.615% Contract Profit and Overhead Charges |  |  |  |  | 1347.5174
11244.8174
| Tender Premium @16.01% |  |  |  |  | 1800.2953
[6 empty] | 9444.5221 | 1No
ii | B) 150MM Dia Gate Valve PN-16
| Basic Rate (as per CSSR-(PH 27-2)-2018-19) | 1 | No | 19577 | 1No | 19577 | (PH-27 S o R-2)
| Add 5% Transportation charges on Basic |  |  |  |  | 978.85
20555.85
| Add 13.615% Contract Profit and Overhead Charges |  |  |  |  | 2798.679
23354.529
| Tender Premium @16.01% |  |  |  |  | 3739.0601
[6 empty] | 19615.4689 | 1No
iiI | C) 400MM Dia Gate Valve PN-16
| Basic Rate (as per CSSR-(PH-27-2)-2018-19) | 1 | No | 216249 | 1No | 216249 | (PH-27 S o R-2)
| Add 5% Transportation charges on Basic |  |  |  |  | 10812.45
227061.45
| Add 13.615% Contract Profit and Overhead Charges |  |  |  |  | 30914.4164
257975.8664
| Tender Premium @16.01% |  |  |  |  | 41301.9362
[6 empty] | 216673.9302 | 1No
2 | Lowering, keeping in position and fixing C.I. sluice valves (with cap / with hand wheel & reflex valves) excluding cost of bolts, nuts, rubber insertion, sluice valve and tail pieces,as directed by Engineer-in-Charge etc., complete for finished item of work, except GST.
i | A) 80MM Dia Gate Valve PN-16
a) Labour
| Labour for laying Sluice Valve with cap , with hand wheel & reflex valve | kgs | 35.47 | 2.57 | kg | 91.1579
| g)Add 13.615% Overhead & Contractors Profit |  | 0.13615 |  |  | 12.4111
103.569
| Deduct 16.01% Tender premium |  | 0.1601 |  |  | 16.5814
[6 empty] | 86.9876 | 1 No
ii | B)150mm dia meter
a)Labour
| Labour for laying Sluice Valve with cap , with hand wheel & reflex valve (72.5+77+90)/3=79.83 | kgs | 79.83 | 2.57 | kg | 205.1631
| g)Add 13.615% Overhead & Contractors Profit |  | 0.13615 |  |  | 27.933
233.0961
| Deduct 16.01% Tender premium |  | 0.1601 |  |  | 37.3187
[6 empty] | 195.7774 | 1 No
iii | C) 400MM Dia meter
a)Labour
| Labour for laying Sluice Valve with cap , with hand wheel & reflex valve (242.4+257+300)/3=266.46 | kgs | 266.46 | 2.57 | kg | 684.8022
| g)Add 13.615% Overhead & Contractors Profit |  | 0.13615 |  |  | 93.2358
[6 empty] | 778.038 | 1 No
| Deduct 16.01% Tender premium |  | 0.1601 |  |  | 124.5639
[6 empty] | 653.4741 | 1 No
3 | Jointing CI pipes, fittings and valves with flanged ends including cost of jointing materials such as bolts, rubber insertion, white lead including filling with water, with lead up to 500 meters and testing to required pressure complete. (Reference to specifications. BIS No.3114/1994.), as directed by Engineer-in-Charge for finished item of wor, except GST.
Details of cost for 10 joints
i | 80mm dia pipe
a) Labour
| Plumber 1st class | day | 0.09 | 540 | day | 48.6
| Plumber 2st class | day | 0.21 | 450 | day | 94.5
| Man mazdoor | day | 0.8 | 425 | day | 340
| Area allowance @ 25% |  | 0 | 483.1 |  | 0
| b) Material |  |  |  |  | 0
| Bolts and nuts 16mm dia 60mm long | kg | 6.8 | 60.5 | kg | 411.4
| Rubber inertion 5mm thick | kg | 2.125 | 107.69 | kg | 228.8413
| While lead |  |  |  |  | 0
| c)Testing | rm | 27.5 | 4.56 | rm | 125.4
| d)Total =a+b+c |  |  |  |  | 1248.7413
| e)Add for Water charges @ 1% on Labour & testing charges |  | 0.01 | 608.5 |  | 6.085
| f)Total=d+e+f |  |  |  |  | 1254.8263
| g)Add 13.615% Overhead & Contractors Profit |  |  |  |  | 170.8446
| Cost for 10 joints |  | 0.13615 |  |  | 1425.6708
| Rate for joint |  |  |  |  | 142.5671
| Deduct Tender premium@16.01% |  | 0.1601 |  |  | 22.825
[6 empty] | 119.7421 | 1No
Details of cost for 10 joints
ii | 150mm dia pipe
a) Labour
| Plumber 1st class | day | 0.18 | 540 | day | 97.2
| Plumber 2st class | day | 0.42 | 450 | day | 189
| Man mazdoor | day | 1.1 | 425 | day | 467.5
| Area allowance @ 25% |  | 0 | 483.1 |  | 0
| b) Material |  |  |  |  | 0
| Bolts and nuts 16mm dia 60mm long | kg | 24 | 60.5 | kg | 1452
| Rubber inertion 5mm thick | kg | 4.3 | 107.69 | kg | 463.067
| While lead |  |  |  |  | 0
| c)Testing | rm | 27.5 | 8.55 | rm | 235.125
| d)Total =a+b+c |  |  |  |  | 2903.892
| e)Add for Water charges @ 1% on Labour & testing charges |  | 0.01 | 988.825 |  | 9.8883
| f)Total=d+e+f |  |  |  |  | 2913.7802
| g)Add 13.615% Overhead & Contractors Profit |  |  |  |  | 396.7112
| Cost for 10 joints |  | 0.13615 |  |  | 3310.4914
| Rate for joint |  |  |  |  | 331.0491
| Deduct Tender premium@16.01% |  | 0.1601 |  |  | 53.001
[6 empty] | 278.0482 | 1No
iii | C) 400MM Dia meter
ii | 400mm dia pipe
a) Labour
| Plumber 1st class | day | 0.24 | 540 | day | 129.6
| Plumber 2st class | day | 0.56 | 450 | day | 252
| Man mazdoor | day | 1.2 | 425 | day | 510
| Area allowance @ 25% |  | 0.25 | 891.6 |  | 222.9
| b) Material |  |  |  |  | 0
| Bolts and nuts 16mm dia 60mm long | kg | 39.6 | 60.5 | kg | 2395.8
| Rubber inertion 5mm thick | kg | 10.28 | 107.69 | kg | 1107.0532
| While lead |  |  |  |  | 0
| c)Testing | rm | 27.5 | 17.1 | rm | 470.25
| d)Total =a+b+c |  |  |  |  | 5087.6032
| e)Add for Water charges @ 1% on Labour & testing charges |  | 0.01 | 1361.85 |  | 13.6185
| f)Total=d+e+f |  |  |  |  | 5101.2217
| g)Add 13.615% Overhead & Contractors Profit |  |  |  |  | 694.5313
| Cost for 10 joints |  | 0.13615 |  |  | 5795.753
| Rate for joint |  |  |  |  | 579.5753
| Deduct Tender premium@16.01% |  | 0.1601 |  |  | 92.79
[6 empty] | 486.7853 | 1No
4 | Centrifugally cast (spun) Ductile Iron pressure pies with flanged (welded) ends for water,gas,sewage conforming to IS: 8329/2000 in standard working lengths of 1,2,3,4,5 mts for classification K9 with cement mortar lining inside the pipes with outside zone coating Rates are ex-factory,excluding transportation & taxes
| CSSR-(PH 21-3)-2018-19 | [5 empty] | PH-21 So R-3
i | A)250mm DIA Flanged Pipes (1Mtr Length) | 1 | Rmt | 8411 | 1Rmt | 8411
| Add 5% Conveyance charges on basic Rate |  |  |  |  | 420.55
8831.55
| Add 13.615% overhead contract profit |  |  |  |  | 1202.4155
[6 empty] | 10033.9655 | 1No
| Tender Premium 16.01% |  |  |  |  | 1606.4379
[6 empty] | 8427.5277 | 1No
ii | B)250mm DIA Flanged Pipes (2Mtr Length) | 1 | Rmt | 11294 | 1Rmt | 11294 | PH-21 So R-3
| Add 5% Conveyance charges on basic Rate |  |  |  |  | 564.7
11858.7
| Add 13.615% overhead contract profit |  |  |  |  | 1614.562
[6 empty] | 13473.262 | 1No
| Tender Premium 16.01% |  |  |  |  | 2157.0692
[6 empty] | 11316.1928 | 1No
iii | C)250mm DIA Flanged Pipes (4Mtr Length) | 1 | Rmt | 16159 | 1Rmt | 16159 | PH-21 So R-3
| Add 5% Conveyance charges on basic Rate |  |  |  |  | 807.95
16966.95
| Add 13.615% overhead contract profit |  |  |  |  | 2310.0502
[6 empty] | 19277.0002 | 1No
| Tender Premium 16.01% |  |  |  |  | 3086.2477
[6 empty] | 16190.7525 | 1No
iv | D)150mm DIA Flanged Pipes (1Mtr Length) | 1 | Rmt | 4845 | 1Rmt | 4845 | PH-21 So R-3
| Add 5% Conveyance charges on basic Rate |  |  |  |  | 242.25
5087.25
| Add 13.615% overhead contract profit |  |  |  |  | 692.6291
5779.8791
| Tender Premium 16.01% |  |  |  |  | 925.3586
[6 empty] | 4854.5204 | 1No
v | E)150mm DIA Flanged Pipes (2Mtr Length) | 1 | Rmt | 6425 | 1Rmt | 6425 | PH-21 So R-3
| Add 5% Conveyance charges on basic Rate |  |  |  |  | 321.25
6746.25
| Add 13.615% overhead contract profit |  |  |  |  | 918.5019
[6 empty] | 7664.7519 | 1No
| Tender Premium 16.01% |  |  |  |  | 1227.1268
[6 empty] | 6437.6252 | 1No
5 | Centrifugally cast (span) Ductile Iron Fittings conforming to IS:9523/2000 having dimensions as per table. The rates mentioned here under are for fitting,zinc coated externally with inside mortor lining (with finishing as per class 13/IS 9523/2000) (ex-works) Excluding Tranportation and Taxes
i | A) DI Fittings upto 300mm Dia (CSSR-(PH-22-1-IV-V-VII)-2018-19) | [5 empty] | (CSSR-(PH-22-1-IV-V-VII)-2018-19)
| Basic Rate | 1 | KG | 105 | 1KG | 105
| Add 5% Conveyance charges on basic Rate |  |  |  |  | 5.25
110.25
| Add 13.615% overhead contract profit |  |  |  |  | 15.0105
125.2605
| Tender Premium @16.01% |  |  |  |  | 20.0542
[6 empty] | 105.2063 | 1KG
6 | Providing and laying of Vibrated Reinforced Cement Concrete corresponding to M-30 grade Design Mix Concrete corresponding to IS 456 using weigh batcher with 20mm size well graded machine crushed hard granite chips (Coarse aggregate) from approved quarry with a minimum cement content of 400 kg/CuM including cost and conveyance of all materials like cement, Coarse aggregate, Fine aggregate, water etc., to site, including centering & shuttering using steel scaffolding pipes, jack props, wallers, foot plates, brackets, steel centering plates weigh batcher etc machine mixing, laying concrete, vibrating, finishing smooth to required levels, curing, pumping to work spot, lifting of material with mechanical equipment like winch, etc., all other incidental and operational charges, all labour charges, etc., but excluding cost of steel and its fabrication charges etc., complete as directed by Engineer-in-Charge for the following finished items of work, excluding GST & seigniorage charges.
Rate for Concrete per 1 Cum, excluding cost of Centering, Shuttering & Steel Reinforcement.
Columns, Lintels, Water Tanks, RCC walls in Buildings -M30 grade
A. Materials:
| Cement | 400 | kgs | 4.3 | / kg | 1720
| 20mm HBG graded metal | 0.8 | cum | 1439.9484 | /cum | 1151.9587
| Sand | 0.2 | cum | 2227.26 | / cum | 445.452
| Rock sand | 0.2 | cum | 937.6984 | / cum | 187.5397
| Water (including for curing)(as per SSR 2017-18) | 1.2 | kl | 73 | /kl | 87.6
B. Machinery
| Batching plant 0.5 cum (6 cum/hr) | 1.333 | hour | 608.1 | / hour | 810.5973
| 40mm needle vibrator hire charges(pg-406) petrol | 1.333 | hour | 205 | / hour | 273.265
C. Labour
| Mason 1st class | 0.167 | No | 470 | each | 78.49
| Mason 2nd class | 0.167 | No | 450 | each | 75.15
| Mazdoor (unskilled) | 5.6 | No | 425 | each | 2380
| Area allowance @ 25% | 0 |  | 2533.64 |  | 0
7210.0527
| Over head charges 13.615% | 0.13615 | % | 7210.0527 |  | 981.6487
| Add VAT 1.75% | 0.0175 | % | 8191.7014 |  | 143.3448
| sundries |  |  |  |  | 0.01
| Rate for 1Cum |  |  |  |  | 8335.0561 | Cum
| Deduct Tender premium@16.01% | 0.1601 |  |  |  | 1334.4425
[6 empty] | 7000.6137 | /1Cum
7 | Supply and Fixing water level indicater containing indicater with suitable probe height with chain pully arrengement and using 15m standard cable as per site reserviour with 250mm dia ball and 40mm squre pipe frame conforming to IS 1230 Drilling hole in roof slab including all accessories etc., complete as directed by the department officers, excluding GST
i | For 500KL ELSR (Quotation) | 1 JOB | 1 | 32550.5 | 1 JOB | 32550.5
| Tender premium@16.01% |  |  |  |  | 5211.335
27339.1649
ii | For 500KL Sump (Quotation) | 1 JOB | 1 | 32550.5 | 1 JOB | 32550.5
| Tender premium@16.01% |  |  |  |  | 5211.335
[6 empty] | 27339.1649 | 1Job
8 | Manifacturing,supply,delivery and fixing at site, the lightening protective system with copper plates and connecters with protective coating,including suitable earthing arrengements as per the standard specifications including cost and conveyance, labour charges etc.,complete as directed by the departmental officers, except GST
i | For 500KL ELSR (Quotation) | 1 JOB | 1 | 30875.5 | 1 JOB | 30875.5
| Tender premium@16.01% |  |  |  |  | 4943.1676
[6 empty] | 25932.3325 | 1Job
ii | For 500KL Sump (Quotation) | 1 JOB | 1 | 29673.5 | 1 JOB | 29673.5
| Tender premium@16.01% |  |  |  |  | 4750.7274
[6 empty] | 24922.7726 | 1Job
9 | Supply and Fixing of SS Railing containing vertical size 40mm thickness 16 gauge at height 1.10M and top horizental pipes 40mm size and thickness 16 gauge and middle 25mm size thickness 16 gauge and including base covers and L Bends and Dummys as per standard requirements including cost and conveyance of all labour charges etc., complete, except GST
i | For 500KL ELSR (Quotation) | 1 Rmt | 1 | 3303.75 | 1 Rmt | 3303.75
| Tender premium@16.01% |  |  |  |  | 528.9304
[6 empty] | 2774.8196 | 1Rmt
ii | For 500KL Sump (Quotation) | 1 Rmt | 1 | 3303.75 | 1 Rmt | 3303.75
| Tender premium@16.01% |  |  |  |  | 528.9304
[6 empty] | 2774.8196 | 1Rmt
iii | Dogg-Legged Staircase (Quotation) | 1 Rmt | 1 | 3303.75 | 1 Rmt | 3303.75
528.9304
[6 empty] | 2774.8196 | 1Rmt
500KL Sump Data
10 | Providing, laying, testing & Commissioning of following classes MS pipes conforming to IS 3589 and 1239 including fittings like elbows, tees, flanges, tapers, nuts, bolts, gaskets etc., complete. Makes : Jindal / Hissar / Tata pipes
i | A)150mm Dia Pipe C Class (CSSR-ELEC 10.7.19.C-2018-19) | [5 empty] | (CSSR-ELEC 10.7.19.C-2018-19)
|  | 1 | Sqm | 2241 | 1Sqm | 2241
| Add 5% Transport Charges from Basic Rate |  |  |  |  | 112.05
2353.05
| Add 13.615% Contract profit and overhead charge |  |  |  |  | 320.3678
2673.4178
| Tender Premium @16.01% |  |  |  |  | 428.0142
[6 empty] | 2245.4036 | 1Sqm
ii | B)250mm Dia Pipe C Class (CSSR-ELEC 10.7.19.a-2018-19) | [5 empty] | (CSSR-ELEC 10.7.19.a-2018-19)
| Basic Rate | 1 | Sqm | 3500 | 1Sqm | 3500
| Add 5% Transport Charges from Basic Rate |  |  |  |  | 175
3675
| Add 13.615% Contract profit and overhead charge |  |  |  |  | 500.3512
4175.3512
| Tender Premium @16.01% |  |  |  |  | 668.4737
[6 empty] | 3506.8775 | 1Sqm
11 | Manfacturing supply delivery lowering laying jointing testing of MS pipe using 8mm thick MS piate including cost and conveyanc of all material and cost oe epoxy painting labour charges and all incidental operation charges complete
i | 400mm Dia MS Pipe (KG amount taken from Market value)
a)weight of MS plate
|  | 3.142*0.408 | 1 | 8 | 7.85 | 80.5056 | KG
| Add 5% Buruing Losses |  |  |  |  | 4.0253
[6 empty] | 84.5309 | KG
| b)Cost of MS Plate |  |  |  | 84.53 | KGS | 48000 | 1MT | 4057.44
| c)Fabrication Charges |  |  |  | 80.51 | KGS | 6.5 | 1KG | 523.315
| d)Epoxy Paint (2x3.14x0.408x1=2.560) |  |  |  | 2.5622 | Sqm | 100 | 1Sqm | 256.224
| e)Transportation charges |  |  |  | 80.51 | KGS | 500 | 1MT | 40.255
| f)Lowering and Laying Charges |  |  |  | 1 | Rmt | 397 | 1Rmt | 397
5274.234
| Add 13.615% overhead and contract profit | [7 empty] | 718.087
5992.321
12 | Cost of M.S Flanges including cost of bolts, nuts, rubber packing etc., complete and flange thickness confirming to IS:7322-1985 and flange dimensions confirming to IS:1538-1993 excluding cost of MS specials including cost and conveyance to site etc., complete.
150mm Dia M.S Flanges
i | A)150mm Dia and 18mm thick (CSSR-(PH 11-5 )2018-19) | [5 empty] | (CSSR-(PH 11 S o R 5 )2018-19)
| Baic Rate | 1 | No | 1588 | 1No | 1588
1588
| Add 13.615% Contract profit and overhead charge |  |  |  |  | 216.2062
1804.2062
| Tender Premium @16.01% |  |  |  |  | 288.8534
[6 empty] | 1515.3528 | 1No
250mm Dia M.S Flanges
i | B)250mm Dia and 18mm thick (CSSR-(PH 11-5 )2018-19) | [5 empty] | (CSSR-(PH 11 S o R 5 )2018-19)
| Baic Rate | 1 | No | 2582 | 1No | 2582
2582
| Add 13.615% Contract profit and overhead charge |  |  |  |  | 351.5393
2933.5393
| Tender Premium @16.01% |  |  |  |  | 469.6596
[6 empty] | 2463.8797 | 1No
400mm Dia M.S Flanges
iii | C)400mm Dia and 18mm thick (CSSR-(PH 11-5 )2018-19) | [5 empty] | (CSSR-(PH 11 S o R 5 )2018-19)
| Baic Rate | 1 | No | 5322 | 1No | 5322
5322
| Add 13.615% Contract profit and overhead charge |  |  |  |  | 724.5903
6046.5903
| Tender Premium @16.01% |  |  |  |  | 968.0591
[6 empty] | 5078.5312 | 1No
13 | Manifacture, Supply and Delivery of R.C.C Spun / Vibrated cast (Reinforced) Socket and Spigot pipes conforming to B.I.S. 458/2003, Cost of Rubber Ring,transportation charges and Including Labour Charges for lowering ,laying,jointing in readymade trenches true to alighenment and Gradient and all incidental operation charges etc complete
i | A)400mm Dia RCC NP-2 Class Pipes (CSSR-PH 3-1-I-18-19) | [5 empty] | (CSSR-PH 3 S o R 1-I-18-19)
| (i)Basic Rate (as per CSSR-PH-2019-20) | 1 | Rmt | 707 | 1Rmt | 707
| (ii)Basic Rate Rubber Ring (142/2.50) | 1 | No | 56.8 | 1No | 56.8 | (CSSR-PH 5 S o R 1-I-18-19)
(iii)Tranporatation charges upto 20Kms
Upto 5KMS=25.03
| 15KMS=15*1.87=28.05 (=25.03+28.05) |  |  |  |  | 53.08 | (CSSR-PH 7 S o R 1-I-18-19)
| (iv)Lowering,laying charges | 1 | Rmt | 23 | 1Rmt | 23 | (CSSR-PH 11 S o R a-I-18-19)
839.88
| Add 13.615% Contract profit and Overhead Charges |  |  |  |  | 114.3497
954.2297
| Tender Premium @16.01% |  |  |  |  | 152.7722
[6 empty] | 801.4575 | 1Rmt
14 | Supply and Fixing of pre-cast RCC Chamber bottom size width 36' Dia and top 21' Dia over CC Bed (1:4:8) including cast and conveyance all material labour charges and incidental charges etc complete
i | Sluice Valve Chambers (Quotation) | 1No | 1 | 4850 | 4850
| Tender premium@16.01% |  |  |  | 776.485
[5 empty] | 4073.515 | 1No
15 | Supply and fixing M.D -10 with 500mm dia clear opening C.I. Manhole frame and cover for 914.4 mm dia chamber (20 Kg- light weight) in the roof of the Sump as shown in the detail drawing with a clear opening of 760 mm dia including cost and conveyance of all materials to site, all labour charges, complete as directed by Engineer-in-Charge for finished item work, except GST.
i | Sluice Valve Chambers (CSSR-(PH-28-1 I-a)-2018-19) | 1No | 1 | 1782 | 1782 | (CSSR-(PH-28 S o R 1 I-a)-2018-19)
| Tender premium@16.01% |  |  |  | 285.2982
[5 empty] | 1496.7018 | 1No
16 | Refilliing foundations and basement with useful excavated soils (other than black cotton soils and other expensive soils) including all labour charges for filling spreading in layers of 15 cm thickness watering breaking clods ramming etc., excluding GST , Complete for finished item of work
Unit=1Cum, Output=6Cum
Non Labour
Labour
| Mazdoor (unskilled) | 0.31 | Day | 425 | Day | 131.75
| Area allowance | 0 |  | 124 |  | 0
131.75
| Add 13.615% Overhead charges & Contract Profit | 0.13615 |  |  |  | 17.9378
| Rate for 6 Cum |  |  |  |  | 149.6878 | /6Cum
| Rate for 1 Cum |  |  |  |  | 24.948
| Sundries |  |  |  |  | 0.05
[6 empty] | 24.998 | /1Cum
| Deduct Tender premium@16.01% |  |  |  |  | 4.0022
[6 empty] | 20.9958 | /1Cum
17 | Centrifugally cast (span) Ductile Iron Fittings conforming to IS:9523/2000 having dimensions as per table. The rates mentioned here under are for fitting,zinc coated externally with inside mortor lining (with finishing as per class 13/IS 9523/2000) (ex-works) Excluding Tranportation and Taxes
i | A) DI Fittings upto 300mm Dia (CSSR-(PH-22-1-IV-V-VII)-2018-19) | [5 empty] | (CSSR-(PH-22-1-IV-V-VII)-2018-19)
| Basic Rate | 1 | KG | 105 | 1KG | 105
| Add 5% Conveyance charges on basic Rate |  |  |  |  | 5.25
110.25
| Add 13.615% overhead contract profit |  |  |  |  | 15.0105
125.2605
| Tender Premium @16.01% |  |  |  |  | 20.0542
[6 empty] | 105.2063 | 1KG
18 | Manfacturing supply delivery of Air valve gauge fabrication of size 1x1x1m using 50x50x6mm MS angles vertical and Horizental frame and fixing 10mm square rods c/c 150mm including cost and conveyanc of all material and cost epoxy painting labour charges and fixing gauge in cement concrete morter and all incidental operation etc complete.
i | a)Weight of MS Angle (50x50x6mm) (Market Value)
| Vertical | 4 | 1.3 | 5.2
| Horizental top and Bottom | 8 | 1 | 8
| Cover Opening with lock arrangement | 4 | 0.6 | 2.4
15.6
| Add 5% Burning Losses |  |  | 0.78
|  |  |  | 16.38 | 4.5KG/1RMT | 73.71 | KGS
b)10mm Squar Rods
| Four sides | 4x2x7 | 1 | 56
| Top | 2x7 | 1 | 14
70
| Add 5% Burning Losses |  |  | 3.5
|  |  |  | 73.5 | 0.78KG/1Rmt | 57.33 | KGS
| c)Cost of MS Angle |  |  |  | 73.71 | KGS | 48000 | 1MT | 3538.08
| Cost of 10mm Squar rods |  |  |  | 57.33 | KGS | 42000 | 1MT | 2407.86
| d)Fabrication Charges |  |  |  | 131.04 | KGS | 19.8 | 1KG | 2594.592
| e)Epoxy Paint Sides (4x1.5x1x1=6) |  |  |  | 7.5 | Sqm | 100 | 1Sqm | 750
Epoxy Paint Top (1.5x1x1=1.5)
| f)Transportation charges | [7 empty] | 1500
| g)Fixing air vlve gauge with cement concrete morter and Laying Charges |  |  |  | 1 | Job | 1500 | 1job | 1500
12290.532
| Add 13.615% overhead and contract profit | [7 empty] | 1673.3559
13963.8879
| Tender Premium@16.01% | [7 empty] | 2235.6185
11728.2695
19 | Plain Cement concrete (M 20) grade using 20mm and 10mm metal using concrete mixer nominal size well graded machine crushed granite stone chips from approved quarry including cost and conveyance and seigniorage charges of all materials like cement, sand coarse aggregate, water etc., to site, cost of seigniorage on materials including centering, shuttering machine mixing, laying concrete, tamping finishing smooth to required levels, curing mall other incidental and operational charges, labour charges etc., complete but excluding cost of steel and its fabrication charges for the following finished item of work.
| Mason 1st class | 0.1 | Nos | 470 | Each | 47
| Mazdoor (Unskilled) | 1.39 | Nos | 425 | Each | 590.75
| Area allowance 40% | 0 |  | 448.55 |  | 0
| Total I |  |  |  |  | 0
| Machinery |  |  |  |  | 0
| Concrete mixer 0.28 Cum | 0.4 | Hour | 608.1 | Hour | 243.24
| Total II |  |  |  |  | 0
| Material |  |  |  |  | 0
| Supply of hand broken crushed course aggregate of grading -III |  |  |  |  | 0
| 20mm Metal | 0.54 | Cum | 1542.2 | Cum | 832.788
| 10mm Metal | 0.36 | Cum | 1275.95 |  | 459.342
| Coarse sand | 0.45 | Cum | 2227.26 | Cum | 1002.267
| Cement | 0.33 | MT | 4300 | MT | 1419
| Total III |  |  |  |  | 4594.387
| Rate for 1 Cum Total(I+II+III) |  |  |  |  | 4594.387
| Over head charges 14% | 0.14 | % | 5124.805 |  | 625.5258
| Add VAT 1.75% | 0.0175 | % | 5842.2777 |  | 80.4018
5300.3146
| Rate for 1Cum |  |  |  |  | 5300.3146
| Deduct Tender premium@16.01% |  |  |  |  | 848.5804
[6 empty] | 4451.7342 | 1Cum
20 | Manufacture, Supply, & Delivery of HDPE fittings conforming to IS 4984 - 1995 including transportation to anywhere in T.G. Excluding taxes
i | A) MS Flanges
225mm Dia (CSSR-PH-16-1(b)-2018-19)
| Baic Rate | 1 | No | 831 | 1No | 831 | (CSSR-PH-16 S o R-1(b)-2018-19)
831
| Add 13.615% Contract profit and overhead charge |  |  |  |  | 113.1406
944.1407
| Tender Premium @16.01% |  |  |  |  | 151.1569
[6 empty] | 792.9837 | 1No
iii | (B) TEES
225mm Dia (CSSR-PH-16-1(e)-2018-19)
| Baic Rate | 1 | No | 4265 | 1No | 4265 | (CSSR-PH-16 S o R-1(e)-2018-19)
4265
| Add 13.615% Contract profit and overhead charge |  |  |  |  | 580.6798
4845.6798
| Tender Premium @16.01% |  |  |  |  | 775.7933
[6 empty] | 4069.8864 | 1No

## Panal Board data
Panel Room
21 | Earth work excavation by Mechanical means for Sump/OHT/Pump Room & Pipe Line trenches and depositing on bank in all types of soils like morum, red earth, gravely soils, ordinary soils upto SDR in all conditions including hire & operational charges of machinery, labour charges for setting out, construction of shoring and bracing, removal of stumps and all other deletarious matter, dressing on sides & bottom of trench in all conditions viz dry, wet and slushy etccomplete for finished item of work as per SS 20 B (APSS 308), except GST.
i | Ordinary soils-Mechnical means-Upto 3m depth
Unit=Cum
Taking output=240 Cum
a)Labour
| Mazdoor (unskilled) | 8.32 | day | 425 | each | 3536
| Area allowance | 0 |  | 3536 |  | 0
3536
b) Machinery
| Hydralic excavator 1 Cum bucket capacity | 6 | hr | 2967.9 | per hr | 17807.4
| Rate per 240 Cum |  |  |  |  | 21343.4 | /240Cum
[6 empty] | 88.9308 | /1Cum
| Overhead charges & Contractors profit @ 13.615% | 0.13615 |  | 88.9308 |  | 12.1079
[6 empty] | 101.0388 | /1Cum
| Deduct Tender premium@16.01% | 0.1601 |  |  |  | 16.1763
[6 empty] | 84.8625 | /1Cum
22 | Earth work excavation by Mechanical means upto 3 mt depth (blasting prohibited) for Pipe Line trenches and depositing on bank in all types of soils like morum, red earth, gravely soils, ordinary soils upto SDR in all conditions including hire & operational charges of machinery, labour charges for setting out, construction of shoring and bracing, removal of stumps and all other deletarious material, dressing on sides & bottom of trench in all conditions viz dry, wet and slushy etc., as directed by Engineer-in-Charge etc., complete for finished item of work as per SS 20 B (APSS 308), except GST.
i | Basic Rate (Data taken from ELSR)) | 1 | Cum | 652.2 | 1Cum | 652.2
| Tender Premium @16.01% |  |  |  |  | 104.4172
[6 empty] | 547.7828 | 1Cum
23 | Plain Cement Concrete (1:4:8) prop.using 40mm nominal size well graded hard broken granite metal from approved quarry including cost and conveyance of all material, all labour charges for machine mixing of concrete, laying concrete, compacting by vibration including curing, finishing top surface to required levels neatly etc., complete as derected by Engineer-in-charge for finished item of work in foundations, excluding GST & seigniorage charges.
i | Labour
| Mason-CI-I | 0.1 | day | 470 | Each | 47
| Mazdoor (Unskilled) | 1.39 | day | 425 | Each | 590.75
| Area allowance | 0 |  | 637.75 |  | 0
637.75
ii | Machinery
| Concrete mixer 10/7 cft (0.2/0.8 cum) capacity | 1 | Hours | 534.3 | Hours | 534.3
534.3
iii | Material
| Cement | 0.162 | Ton | 4300 | Ton | 696.6
| Coarse aggrigate (40mm Metal) | 0.9 | Cum | 1085.95 | Cum | 977.355
| Coarse sand | 0.225 | Cum | 2227.26 | Cum | 501.1335
| Rock sand | 0.225 | Cum | 937.7 | Cum | 210.9825
| Cost of water RURAL | 1.2 | KL | 73 | KL | 87.6
2473.671
| Rate for 1 Cum (i+ii+iii) |  |  |  |  | 3645.721
| Overhead charges & Contractors profit @ 13.615% | 0.13615 |  | 3645.721 |  | 496.3649
[6 empty] | 4142.0859 | /1Cum
| Deduct Tender premium@16.01% | 0.1601 |  |  |  | 663.148
[6 empty] | 3478.938 | /1Cum
24 | Providing and laying of Vibrated Reinforced Cement Concrete corresponding to M-30 grade Design Mix Concrete corresponding to IS 456 using weigh batcher with 20mm size well graded machine crushed hard granite chips (Coarse aggregate) from approved quarry with a minimum cement content of 400 kg/CuM including cost and conveyance of all materials like cement, Coarse aggregate, Fine aggregate, water etc., to site, including centering & shuttering using steel scaffolding pipes, jack props, wallers, foot plates, brackets, steel centering plates weigh batcher etc machine mixing, laying concrete, vibrating, finishing smooth to required levels, curing, pumping to work spot, lifting of material with mechanical equipment like winch, etc., all other incidental and operational charges, all labour charges, etc., but excluding cost of steel and its fabrication charges etc., complete as directed by Engineer-in-Charge for the following finished items of work, excluding GST & seigniorage charges.
Rate for Concrete per 1 Cum, excluding cost of Centering, Shuttering & Steel Reinforcement.
Columns, Lintels, Water Tanks, RCC walls in Buildings -M30 grade
A. Materials:
| Cement | 400 | kgs | 4.3 | / kg | 1720
| 20mm HBG graded metal | 0.8 | cum | 1439.9484 | /cum | 1151.9587
| Sand | 0.2 | cum | 2227.26 | / cum | 445.452
| Rock sand | 0.2 | cum | 937.6984 | / cum | 187.5397
| Water (including for curing)(as per SSR 2017-18) | 1.2 | kl | 73 | /kl | 87.6
B. Machinery
| Batching plant 0.5 cum (6 cum/hr) | 1.333 | hour | 608.1 | / hour | 810.5973
| 40mm needle vibrator hire charges(pg-406) petrol | 1.333 | hour | 205 | / hour | 273.265
C. Labour
| Mason 1st class | 0.167 | No | 470 | each | 78.49
| Mason 2nd class | 0.167 | No | 450 | each | 75.15
| Mazdoor (unskilled) | 5.6 | No | 425 | each | 2380
| Area allowance @ 25% | 0 |  | 2533.64 |  | 0
7210.0527
| Over head charges 13.615% | 0.13615 | % | 7210.0527 |  | 981.6487
| Add VAT 1.75% | 0.0175 | % | 8191.7014 |  | 143.3448
| sundries |  |  |  |  | 0.01
| Rate for 1Cum |  |  |  |  | 8335.0561 | Cum
| Deduct Tender premium@16.01% | 0.1601 |  |  |  | 1334.4425
[6 empty] | 7000.6137 | /1Cum
25 | Centring and Scaffolding charges for RCC members including all materials and Labour charges for forming and removing etc., complete as directed by Engineer-in-Charge for finished item of work. Except GST
Columns,Braces and Roof Slab
Above Ground Level
i | Shuttering Rate: | 1 | Sqm | 1332 | 1Sqm | 1332
1332
| Overhead Charges & Contract Profit@13.615% |  |  |  |  | 181.3518
1513.3518
| Deduct Tender Premium @16.01% |  |  |  |  | 242.2876
[6 empty] | 1271.0642 | 1Sqm
26 | Providing High Yield Strength Deformed (HYSD)/ Thermo Mechanically Treated (TMT) steel bars (Fe 415 grade as per IS 1786-1979) upto 36mm dia for RCC and RCM works including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and size and tying and lap-splicing with binding wire of 18 SWG, forming grills for reinforcement work as per approved designs and drawings including cost and conveyance of steel bars including all wastages such as overlaps, couplings, chairs, spacer bars including cost and conveyance of binding wire, cover blocks and all incidental, operational, all labour charges such as cutting, bending, placing in position, tying etc., complete for finished item of work, as directed by Engineer-in-Charge (APSS No.126), excluding GST and seignorage charges.
Unit; 1MT,Output:1MT BLD-CSTN-4-1
i | Material
| HYSD/TMT Bars including 5% for overlaps and wastage | 1.05 | MT | 45000 | 1MT | 47250
| Binding wire | 6 | Kg | 50 | kg | 300
47550
ii | Labour for cutting,bending,shifting to site,tying,lap splicing and placing in poition
| 1st class Blacksmith/Barbender | 3 | day | 565 | day | 1695
| 2nd class Blacksmith/Barbender | 7 | day | 470 | day | 3290
| Mazdoor(Unskilld) | 10 | day | 425 | day | 4250
| Area allowance | 0 |  | 12525 |  | 0
9235
| Rate for 1 MT |  |  |  |  | 56785 | /1MT
| Rate for 1 Kg |  |  |  |  | 56.785 | /1Kg
| Overhead charges and Contract Profit@13.615% |  |  |  |  | 7.7313
| Rate for 1 Kg |  |  |  |  | 64.5163
| Rate for 1 MT |  |  |  |  | 64516.2778 | /1MT
| Tender Premium @16.01% |  |  |  |  | 10329.0561
[6 empty] | 54187.2217 | 1MT
27 | Re filling foundation/ basement /pipe line trenches with useful excavated soils (other than black cotton soils and other expansive soils) with initial lead and lifts spreading in layers not exceeding 150mm thick, consolidating each deposited layer by watering and ramming, compacting by earth mover to achieve optimum moiture content including cost and conveyance of water to work site and all operational, incidental, all labour charges, hire charges of T&P etc., complete for finished item of work, as directed by Engineer-in-charge (APSS No. 309 & 310), except GST.
Unit=cum, Taking output=6 Cum BLD-CSTN 3-1, P.No-19
Refilling with excavated earth
| Mazdoor | 3.12 | day | 425 | Each | 1326
| Area allowance | 0 | % | 1326 |  | 0
| Rate per 6 Cum |  |  |  |  | 1326 | /6Cum
| Rate per 1 Cum |  |  |  |  | 221 | /1Cum
| Over head charges 13.615% | 0.13615 | % | 221 |  | 30.0892
[6 empty] | 251.0891 | /1Cum
| Deduct Tender premium@16.01% | 0.1601 |  |  |  | 40.1994
[6 empty] | 210.8898 | /1Cum
28 | RR masonry in CM (1:6) using hard granite stone from approved quarry including cost and conveyance, seigniorage of all materials, water, all labour charges for dressing stones to required size and shape mixing of cement mortar, wall construction,scaffolding charges, etc., excluding GST, Complete for finished item of work
Unit = 1Cum, Output=1Cum
Labour
| Mason 1st Class | 1.2 | Day | 470 |  | 564
| Mazdoor(unskilled) | 2 | cum | 425 | cum | 850
| Area Allowance @ 0% | 0 |  | 1364 | Nos. | 0
Material
| Sand for Morter | 0.33 | day | 2417.26 | day | 797.6958
| RR Stone Granite | 0.5 | day | 721 | day | 360.5
| Cement OPC (43/53grd) | 0.0792 | MT | 4300 |  | 340.56
| CR Stone Granite | 0.44 |  | 731.95 |  | 322.058
| Bond stones 7 No's-(600x200x200) | 0.16 |  | 1691.28 |  | 270.6048
| Rate per 1Cum |  |  |  |  | 3505.4186
| Over Head and Contractor's Profit @13.615% | 0.13615 |  | 322.058 |  | 43.8482
4141.9296
| Sundries |  |  |  |  | 0.070403
| Rate per cum |  |  |  |  | 4142 | /1Cum
| Deduct Tender premium@16.01% |  |  |  |  | 663.1342
[6 empty] | 3478.8658 | /1Cum
29 | Providing Brick Masonry work in CM(1:6) prop with flyash cement solid blocks of size 290x225x140 mm and compresive strength not less than 50Kg/sqm including cost and conveyance of all materials, labour charges, seigniorage charges, scaffolding and curing, etc., excluding GST, complete for wall.
i | A. MATERIALS:
| No of Fly ash Solid Bricks of Size 290x225x140 required for 1 cum of masonry - TBSC. A.II - 08 | 110 | No.s | 25 | Each | 2750
| Cement Mortar (1:6)-BLD-CSTN-1-7 | 0.1 | cum | 3655.12 | cum | 365.51
B. LABOUR:
| Mason 1st Class | 0.42 | day | 470 | Each | 197.4
| Mason 2nd Class | 0.92 | day | 450 | Each | 414
| Man Mazdoor | 0.7 | day | 425 | Each | 297.5
| Women Mazdoor | 2.1 | day | 425 | Each | 892.5
| Area Allowance@0% | 0 |  | 1801.4 |  | 0
4916.91
| Over head charges & Contractors profit @13.615% | 0.13615 |  | 4916.91 |  | 669.4373
5586.3473
0.052704
| Grand Total |  |  |  | Say Rs. | 5586.4 | /1 Cum
| Deduct Tender premium@16.01@ |  |  |  |  | 894.3826
[6 empty] | 4692.0174 | /1 Cum
30 | Supply & fixing of Rolling shutter made of 80 x 1.25 mm machine rolled CRCA laths, interlocked together through their entire length and jointed together at the ends by end-locks, mounted on specially designed pipe shaft of 50mm Diameter nominal bore MS B class pipe with brackets, plates, guide channels, stoppers, bottom locking plates and arrangements for inside & outside locking with push-pull operations including cost of hood cover and springs complete, painted with one coat of approved steel primer, locks, ball bearings, all accessories etc complete for finished item of work as per special Spec: 110
i | Basic Rate (CSSR-PH-TBSC-E.1-01-2018-19) | 1 | Sqm | 3890 | 1Sqm | 3890 | (CSSR-PH-TBSC-E.1-01-2018-19)
| Add 5% Transport Charges from Basic Rate |  |  |  |  | 194.5
4084.5
| Add 13.615% Contract profit and overhead charge |  |  |  |  | 556.1047
4640.6047
| Tender Premium @16.01% |  |  |  |  | 742.9608
[6 empty] | 3897.6439 | 1Sqm
31 | Plastering in 12mm thick to even faces of brick wall surfaces in two coats with base coat in CM (1:6) 8mm thick and top coat in CM (1:4) 4mm thick with dubara sponge finishing including cost and conveyance of all materials like cement, sand, water etc., to site including all operational & incidental charges, seigniorage charges and all labour charges for mixing mortar, finishing, scaffolding, lift charges, curing, including cutting grooves wherever necessary etc., excluding GST, complete for finished item of work.
Unit=Sqm, Output=10Sqm
Labour
| Mazdoor(unskilled) | 3.9 | Day | 425 |  | 1657.5
| Mason 1st class | 0.63 | Day | 470 |  | 296.1
| Mason 2nd class | 1.47 | Day | 450 |  | 661.5
| Unit=Cum | 0 |  | 2615.1 |  | 0
Material
Base Coat-(1:6) 8mm thick
| Sand for Mortar BLD-CTN-1-7 | 0.11 | Cum | 3655.12 |  | 402.06
| Cement OPC(43/53grd) | 0.0317 | Mt | 4300 |  | 136.31
Top Coat-(1:4) 4mm thick
| Sand for Mortar | 0.04 | Cum | 2417.26 |  | 96.69
| Cement OPC(43/53grd) | 0.0192 | Mt | 4300 |  | 82.56
3332.72
| Taking output=240 Cum | 0% |  | 3332.72 |  | 0
| Rate per 10 Sqm |  |  |  |  | 3332.72
| Rate per 1 Sqm |  |  |  |  | 333.272
| Sundries |  |  |  |  | 0.028
[6 empty] | 333.3 | /1 Sqm
| Add 13.615% Overhead & Contract profit | 0.13615 |  |  |  | 45.3788
378.6788
| Deduct Tender Primium@16.01% |  |  |  |  | 60.6265
[6 empty] | 318.0523 | /1 Sqm
32 | BLD-CSTN-13-16 - Supply and fixing Teak Wood framed FLUSH Doors single shutter door with flush shutter as per approved drawings with best quality 2nd class teakwood frame od size 115x65mm and flush door shutters of 30 mm thick solid bond wood block board typer with teak veneer on one face and commercial ply on another face (One side Teak) teak wood internal lipping as per drawing including fixing of 6 Nos. MS Z hold fasts of size 300 x 40 x 5mm size including cost of Powder Coated/ Chromium Plated Mild Steel fixtures of 3 Nos. butt hinges 150 x 31.75 x 3.5 mm, 2 No tower bolt of 250x12mm dia, 1 No.CP Aldrops - 300 mm long and 2 Nos. CP handles of 150 mm size & 1 No. 63 mm long door stopper including fixing the fixtures to door with required no. of brass screws, bolts and nuts including labour charges for fixing the frame in position, fixing the shutter to the frame etc., complete for finished item of work as per APSS 1001 & 1002 (0.90x2.15)
Unit-1.94 Sqm
Material
| TBSC-D.I-02 Medium Teak Wood scantlings: 2.0 to 3.0 M | 0.0313 | Cum | 80689 | 1 | Cum | 2525.5657 | CSSR-Building items 2018-19
| TBSC-D.I-01 Medium Teak Wood scantlings: 2.0 M | 0.0074 | Cum | 72620 | 1 | Cum | 537.388
| TBSC-L.II-10 Flush door shutters, solid bond wood block board type with teak venner on one face and commercial ply on another face (lipping) : 30 mm thick conforming | 1.935 | Sqm | 2046 | 1 | Sqm | 3959.01
| Furniture Market Hold fasts (300*10*5mm) | 6 | No | 15 | 1 | No | 90
| TBSC-P.II-12 MS-Powder Coated Butt hinges (IS:205)-150mm Long | 3 | No | 40 | 1 | No | 120
| TBSC-P.IV.09 MS-Powder Coated Aldrop (IS:2681) - 300mm long | 1 | No | 164 | 1 | No | 164
| TBSC-P.I-17 MS-Powder Coated Tower Bolt-10mm Bolt (IS:204) 250mm Long | 2 | No | 68 | 1 | No | 136
| TBSC-P.III.06 MS-Powder Coated Door Handles (IS:208) 150 mm long | 2 | No | 45 | 1 | No | 90
| BMT-G.53 MS-Powder Coated - Door Stoppers | 1 | No | 49 | 1 | No | 49
| Market - Rubber bush | 1 | No | 10 | 1 | No | 10
| Man powder CMM-046 - Carpenter CI-II / Erector shuttering | 0.76 | day | 450 | 1 | No | 342
| CMM-087 Light mazdoor | 0.38 | day | 425 | 1 | No | 161.5
8184.4637
| TBSC-T.1-25 Labour charges for fixing flush door shutters of any thickness to the existing door frame including fixing the fixturesto the door shutter excluding cost of shutter | 1.935 | Sqm | 426 | 1 | Sqm | 824.31
9008.7737
| Add 13.615% overhead and contractor profit |  |  | 13.61% |  |  | 1226.5445
| Rate for 1.94 Sqm | [5 empty] | 10235.3182
| Rate per 1 Sqm | 5275.9372
| Deduct Tender Premium@16.01% | [5 empty] | 844.6776
[7 empty] | 4431.2597 | Sqm
33 | Ceramic wall tiles supply of glazed red or white fully body ceramic wall tilws of size 200 x 300 mm /245 mm x 325 mm and thickness 6mm 1st quality, set over CSTN-9- over a base coat of cement mortar (1:8) prop., 12 mm thick and filling the joints with 3mm Nylon spacers at each corner of the tile and joints grooted with laticrete epoxy grout of pigment of approved shade of tiles over a wall. or R.C.C. slab, including cost and conveyance of all materials like cement, sand, water, tiles, white cement etc., to site (excluding cost of C.C. bed) cost of excluding seigniorage on all materials cost of base coat and all labour charges for mixing of cement mortar, laying tiles to required slope as directed by the Ebgineer-in-charge curing etc., complete for finished item of work, IS 13711, IS:13712 IS 13713
|  |  | Unit-10 Sqm |  |  |  |  | CSSR-Building items 2018-19
Material
| As per TBSC-C.II-02 Sl.No. 43 Pg.No.20 CSSR 2015-16 | 10.5 | 1 Sqm | 300 | 1 | Sqm | 3150
| BLC - 001 Cement 43 Gr (including loading charges) | 21.6 | 1 Kg | 4300 | 1 | MT | 92.88
| BLC-001 Cement Slurry | 33 | 1 Kg | 4300 | 1 | MT | 141.9
| BMS-W.68 White cement | 6 | 1 Kg | 30 | 1 | Kg | 180
| BLC-008 Cost of sand | 0.14 | Cum | 2417.2 | 1 | Cum | 338.408
| Man power CMM-001 Mason Cl-I / Brick layer CI-I | 0.96 | day | 470 | 1 | No | 451.2
| CMM-077 Mason CI-II / Brick layer CI-II | 2.24 | day | 450 | 1 | No | 1008
| CMM-087 Light mazdoor | 3.3 | day | 425 | 1 | No | 1402.5
| Area Allowance | 0.25 |  | 2861.7 |  |  | 715.425
| Add water charges 1% |  |  | 73 |  |  | 0.73
7481.043
| Add 13.615% overhead and contractor profit |  |  | 13.61% |  |  | 1018.544
| Rate per 10 Sqm | 8499.587
| Rate for 1 Sqm | 849.9587
| Deduct Tender Premium@16.01% | [5 empty] | 136.0784
[7 empty] | 713.8803 | Sqm
34 | Painting to new walls with two or more coats of Water proof cement paint of approved make, shade and colour to give uniform shade to all plastered surfaces of walls over a base coat of approved cement, primary grade making 3 coats of white cement (total 3 or more coats) in all to give an even shade after thoroughly brushing the surface to remove all dirt and remains of loose powedered materials including cost and conveyance of all materials to work site, and all labour charges such as preparation of the wall surface, applying priming coat, applying water proof cement paint two or more coats, curing, scaffolding etc., complete as directed by Engineer-in-Charge for finished item of work as per SS 912, except GST.
| Unit:Sqm Output : 10 Sqm |  |  | BLD-CSTN-12-5
Material
| White Cement (TSBC-R.1-01) | 1 | Kg | 29 | Kg | 29
| Water proofing Cement Paint (TBSC G-II.04) | 3.5 | Kg | 51 | Kg | 178.5
207.5
C. Labour
| Mason 1st Painter | 0.36 | No | 540 | each | 194.4
| Mason 2nd Painter | 0.84 | No | 450 | each | 378
| Mazdoor (unskilled) | 1.5 | No | 425 | each | 637.5
| Area allowance @ 25% | 0 |  | 1209.9 |  | 0
1209.9
| Rate for 10 Sqm(i+ii) |  |  |  |  | 1417.4 | /10Sqm
| Rate for 1 Sqm |  |  |  |  | 141.74 | /1Sqm
| Add 13.615% Overhead & Contract profit |  |  |  |  | 19.2979
| Rate for 1 Sqm |  |  |  |  | 161.0379 | /1Sqm
| Deduct Tender Primium@16.01% |  |  |  |  | 25.7822
[6 empty] | 135.2557 | /1 Sqm
35 | Providing imperious / weather proof coarse over RCC roof slabs with CM (1:3) with an average thickness of 20mm thick premixed with water proofing compound like ACCO proof or any other ISI make at one KG per bag of cement as prescribed by the manufacturer and laid over the proof slab to required slopes as directed by the engineer in charge when slab is in green including cost and conveyance of all material to site all labour charges and for all operation maintaining necessary slope finishing smooth and lining curing etc complete
Unit:Sqm Output : 10 Sqm
Material
| CM(1:3) | 0.21 | Cum | 4687.12 | Cum | 984.2952
| Water proofing compound | 2 | Kgs | 79 | Kgs | 158
1142.2952
C. Labour
| Mason 1st class | 0.66 | No | 470 | each | 310.2
| Mason 2nd class | 1.54 | No | 450 | each | 693
| Mazdoor (unskilled) | 3.7 | No | 425 | each | 1572.5
| Area allowance @ 25% | 0 |  | 2575.7 |  | 0
2575.7
| Rate for 10 Sqm(i+ii) |  |  |  |  | 3717.9952 | /10Sqm
| Rate for 1 Sqm |  |  |  |  | 371.7995 | /1Sqm
| Add 13.615% Overhead & Contract profit |  |  |  |  | 50.6205
| Rate for 1 Sqm |  |  |  |  | 422.42 | /1Sqm
| Deduct Tender Primium@16.01% |  |  |  |  | 67.6294
[6 empty] | 354.7906 | /1 Sqm
36 | Supplying and fixing of Unplasticised Poly Vinyl Chloride (UPVC) sliding windows two track sliding duly manufactured using UPVC reinforced profiles of (62 mm x 60 mm)/(60 mm x 45 mm) / (60 mm x 52 mm) x 2.0 mm for outer frames, (66 mm x 38 mm) / (58 mm) x 39 mm)/ (60 mm x 42 mm) x 2.0 mm for sliding shutter frames capable of mounting single glazing system, structurally reinforced with hot dip galvanized up to 50 micros of minimum thickness of 1.2 mm prefabricated & welded through fusion welding the window sash shall be fitted with 5 mm thick clear float glass of reputed make duly fixed with TPV Gaskets/EPDM weathering seal resistant accessories like locking system 1 No., per set of sashes and the system is to be installed at the site using anchor fasteners, silicon rubber sealent, easy glazing/ deglazing at site etc., including cost and conveyance of all materials, accessories, labour charges for transportation, erection at site with templates for casement sizing complete for finished item of work.
|  | Unit-1Sqm | [5 empty] | CSSR-Building items 2018-19
| As per TBSC-M.II-09 Sl.No. 529 Pg.No.84 CSSR 2018-19 |  |  | 6375 | 1 | Sqm | 6375
| Add 13.615% overhead and contractor profit |  |  | 13.61% |  |  | 867.9562
| Rate per 1 Sqm | 7242.9563
| Deduct Tender Primium@16.01% |  |  |  |  | 1159.5973
[6 empty] | 6083.359 | /1 Sqm
SANITARY ITEMS
37 | Supplying laying jointing and testing 101.6mm SWG SP-1 pipes of ISI Make confirming to ISI 651 & 4127 with airtight cement joints in CM 1:5:1 prop. Including excavation of trenches and socket pits in any soil(except rock requiring blasting) upto 914.4 mm(3"0') depth and refilling with watering and tamping
Unit-1Rmt
| As per TBSP-A.I-02 Sl.No.2 Pg.No.121 CSSR 2015-16 |  |  | 423 | 1 | Rmt | 423 | CSSR-Building items 2018-19
ADD 40% Lbour component
| Add 13.615% overhead and contractor profit |  |  | 13.61% |  |  | 57.5914
480.5915
480.59
| Deduct TP@16.01% |  | 16.01 | 76.9425
| Rate per 1 RMT |  |  | 403.6475
38 | Supplying and fixing 150 mm x 100 mm SWG gully traps confirming to ISI 651 & 4127 with C.I. grating & Cost brick masonry in CM 1:6 prop.. Intermediate chamber and fitted with 304.8mm x 288.6mm (12"x9") C.I. Frme and hinged cover.
Unit-1No.
| As per TBSP-A.I-09 Sl.No.9 Pg.No.122 CSSR 2015-16 |  |  | 619 | 1 | No | 619 | CSSR-Building items 2018-19
| Add 13.615% overhead and contractor profit |  |  | 13.61% |  |  | 84.2768
703.2768
| Rate per 1 No. | 703.28
| Deduct TP@16.01% |  | 16.01 | 112.5951
| Rate per 1 No. |  |  | 590.6849
39 | Constructing 904.0mm (3"0') dia solid brick masonry inspection chamber as per IS - 4111: Part-1: 1986 with cement mortar (1:6) prop. Using 2nd class clay bricks of 225mm thick from approved source having a minimum crushing strength of 5 N/ Sq.mm including plastering with cement mortar 1:3 prop; 1/2" thick both inside and outside fitted with 20" dia RCC Manhole covers and frames including excavating pits upto a depth of 904mm (3'-0") in all sorts of soils ( excluding rock) and laying cement concrete (1:4:8) 150mm thick using 40mm HBG Metal and PCC 1:2:4 benching and channel 100 mm thick as per standard specification and including cosrt and conveyance of all materials like cement,sand , bricks, water etc.m, to site, cost of seigniorage charges on all materials and all incidentall and operational, labour charges like mixing cement mortar , constructing masonry, lift charges curing, etc., complete for finished item of work as per standard specification.
Unit-1No.
| As per TBSP-B.I-03 Sl.No.76 Pg.No.126 CSSR 2015-16 |  |  | 7321 | 1 | No | 7321 | CSSR-Building items 2018-19
| Add 13.615% overhead and contractor profit |  |  | 13.61% |  |  | 996.7541
8317.7542
8317.75
| Deduct TP@16.01% |  | 16.01 | 1331.6718
| Rate per 1 Sqm |  |  | 6986.0782
40 | Supply and fixing of approved make Orissa pan white glaze W.C. ist quality ISI Marked confirming to IS:2556 -Part-3-2004 with "P" or "S" Trap : 580mm x 440mm duly provading construction brick masonry and CC squatting plate including cost and conyence of all materials and labour charges etc complete as per standard practice for finished item.
Unit-1No.
| As per TBSP-E.I-03 Sl.No.249 Pg.No.135 CSSR 2015-16 |  |  | 1306 | 1 | No | 1306 | CSSR-Building items 2018-19
Provding BrickMasonry seat for Orissa pan/Indian W.C using traditional comman burnt clay bricks as per standard practice.
| As per TBSP-E.I-06 |  |  | 271 | 1 | No | 271
1577
| Add 13.615% overhead and contractor profit |  |  | 13.61% |  |  | 214.7086
1791.7086
1791.71
| Deduct TP@16.01% |  | 16.01 | 286.8528
| Rate per 1 NO. |  |  | 1504.8572
41 | Supplying and fixing low down porcelain flushing tank with lid 10Lit capacity with internal components
Unit-1No.
| As per TBSP-E.IV-01 Sl.No.263 Pg.No.137 CSSR 2015-16 |  |  | 2089 | 1 | No | 2089 | CSSR-Building items 2018-19
| Add 13.615% overhead and contractor profit |  |  | 13.61% |  |  | 345.0041
2879.0041
| Deduct TP@16.01% |  | 16.01 | 460.9286
| Rate per 1 NO. |  |  | 2418.0755
42 | Supplying and fixing Indian make Flat Back Wash Hand Basin 1st quality confirming to IS: 2556-Part-4:1972 with waste fittings like rubber plug , chain, 32mm nominal size C.P. Fitting with parallel pipe thread confirming to IS: 2963-1979 and fitted with 15mm nominal bore Chromium Plated Pillar Tap og 1st quality Indian make 400 grams complete with standard CI Brackets including wooden block : 630x 450mm - Single C.P. Pillar cock
Unit-1No.
| As per TBSP-E.VI-02 Sl.No.269 Pg.No.137 CSSR 2015-16 |  |  | 1981 | 1 | No | 1981 | CSSR-Building items 2018-19
| Add 13.615% overhead and contractor profit |  |  | 13.61% |  |  | 269.7131
2250.7132
2250.71
| Deduct TP@16.01% |  | 16.01 | 360.3387
| Rate per 1 No. |  |  | 1890.3713
43 | Supply and fixing of 90mm dia single socket PVC/SWR Pipe- 4kg/sqm including cost and conveyance of all material labour charges etc.,
Unit-1Rmt
| As per TBSP-H.I-02 Sl.No.461 Pg.No.148 CSSR 2015-16 | 405.00/3 |  | 135 | 1 | Rmt | 135 | CSSR-Building items 2018-19
| Add 13.615% overhead and contractor profit |  |  | 13.61% |  |  | 18.3803
153.3802
| Rate per 1 Rmt | 153.38
| Deduct TP@16.01% |  | 16.01 | 24.5561
| Rate per 1 Rmt |  |  | 128.8239
44 | Supply of rubber lubricant 500 grams UPVC/SWR Pipe fittings
Unit-1No.
| As per TBSP-H.III-03 Sl.No.602 Pg.No.153 CSSR 2015-16 |  |  | 117 | 1 | No | 117 | CSSR-Building items 2018-19
| Add 13.615% overhead and contractor profit |  |  | 13.61% |  |  | 15.9295
132.9296
132.93
| Deduct TP@16.01% |  | 16.01 | 21.2821
| Rate per 1 No. |  |  | 111.6479
45 | S&F 20 mm Nominal Bore GI Pipe Medium grade properties & weight as per IS 1239 ISI Markwith GI Fittings including the cost of pipe and its fittings & labour charges complete
Unit-1Rmt
| As per TBSP-G.I-08 Sl.No.400 Pg.No.145 CSSR 2015-16 |  |  | 204 | 1 | No | 204 | CSSR-Building items 2018-19
| Add 13.615% overhead and contractor profit |  |  | 13.61% |  |  | 27.7746
231.7746
231.77
| Deduct TP@16.01% |  | 16.01 | 37.1064
| Rate per 1 RMT |  |  | 194.6636
46 | S&F 25 mm Nominal Bore GI Pipe Medium grade properties & weight as per IS 1239 ISI Markwith GI Fittings including the cost of pipe and its fittings & labour charges complete
Unit-1Rmt
| As per TBSP-G.I-09 Sl.No.401 Pg.No.146 CSSR 2015-16 |  |  | 268 | 1 | No | 268 | CSSR-Building items 2018-19
| Add 13.615% overhead and contractor profit |  |  | 13.61% |  |  | 36.4882
304.4882
304.49
| Deduct TP@16.01% |  | 16.01 | 48.7488
| Rate per 1 Rmt |  |  | 255.7412
47 | S&F of 15mm brass body CP finish bib tap of not less than 300 grams weight with quarter turn spindle with either internal or external threaded connection confirming to IS 8931
|  | Unit-1No. | [5 empty] | CSSR-Building items 2018-19
| As per TBSP-F.I-02 Sl.No.301 Pg.No.140 CSSR 2015-16 |  |  | 543 | 1 | No | 543
| Add 13.615% overhead and contractor profit |  |  | 13.61% |  |  | 73.9295
616.9294
616.93
| Deduct TP@16.01% |  | 16.01 | 98.7705
| Rate per 1 No. |  |  | 518.1595
48 | S&F of 15mm brass body CP finish pillar tap of not less than 300 grams weight screw type(full turn) confirming to IS 8931
Unit-1No.
| As per TBSP-F.II-01 Sl.No.308 Pg.No.141 CSSR 2015-16 |  |  | 568 | 1 | No | 568 | CSSR-Building items 2018-19
| Add 13.615% overhead and contractor profit |  |  | 13.61% |  |  | 77.3332
645.3332
645.33
| Deduct TP@16.01% |  | 16.01 | 103.3173
| Rate per 1 No. |  |  | 542.0127
49 | S&F of 15mm brass angle stop valve of qurter turn spindle type of not less than 400 grams weight with internal threaded connection confirming to IS 8931
|  | Unit-1No. | [5 empty] | CSSR-Building items 2018-19
| As per TBSP-F.IV-07 Sl.No.330 Pg.No.142 CSSR 2015-16 |  |  | 551 | 1 | No | 551
| Add 13.615% overhead and contractor profit |  |  | 13.61% |  |  | 75.0186
626.0186
626.02
| Deduct TP@16.01% |  | 16.01 | 100.2258
| Rate per 1 No. |  |  | 525.7942
50 | Supplying and fixing of 15mm nom,inal size PVC Connection with brass union nut C.P. Coated
|  | Unit-1No. | [5 empty] | CSSR-Building items 2018-19
| As per TBSP-H.II-14 Sl.No.517 Pg.No.150 CSSR 2015-16 |  |  | 95 | 1 | No | 95
| Add 13.615% overhead and contractor profit |  |  | 13.61% |  |  | 12.9342
107.9342
| Deduct TP@16.01% |  | 16.01 | 17.2803
| Rate per 1 No. |  |  | 90.654
51 | Providing & Placing on terrace ( at all floor levels) polyethylene water storage tank with Double layer approved brand & manufacture with cover and suitable locking arrangement & making necessary holes for inlet & outlets and overflow pipes but without fittings & base support for tanks
Unit-1Ltr
| As per TBSP-H.II-01 Sl.No.504 Pg.No.150 CSSR 2015-16 |  |  | 7 | 1 | Liter | 7 | CSSR-Building items 2018-19
| Add 13.615% overhead and contractor profit |  |  | 13.61% |  |  | 0.95305
7.95
| Deduct TP@16.01% |  | 16.01 | 1.2728
| Rate per 1 No. |  |  | 6.6772
52 | Supplying & Fixing white glazed flat back half stall urinals 1st quality conforming to IS:2556-1995 with standard C.P. Spreader fixed with screws complete Indian make : 590 x 375 x 390 mm
| Basic Rate As per TBSP-E.VII-03 S |  |  | 2555 | 1 | Each | 2555 | CSSR-Building items 2018-19
| Add 13.615% overhead and contractor profit |  |  | 0.13615 |  |  | 347.8632
2902.8632
| Deduct Tender Premium@16.01% |  |  | 0.1601 |  |  | 464.7484
[7 empty] | 2438.1148 | /Each
Motors Supplimentary Items
53 | Supply, delivery and fixing of 20 HP 3 phase 415 Volts submersible monoblock horizontle booster pump set with a Head of 25 Mts. to discharge 37LPS of Lubi/texmo including cost and conveyance of all materials and labor charges etc complete as directed by the TSSC Engineers.
| Electric motor 20HP Double Shaft (CSSR-MRC-2-2018-19) | [5 empty] | (CSSR-MRC-2-2018-19)
| Basic Rate | 1 | No | 104000 | 1No | 104000
| Add 5% Transport charges on Basic |  |  |  |  | 5200
109200
| Add 13.615% Contract Profit and Overhead Charges | 0.13615 | % |  |  | 14867.58
124067.58
| Deduct Tender Premium@16.01% | 0.1601 | % |  |  | 19863.2196
[6 empty] | 104204.3604 | 1No
54 | Supply of 4-Sq-mm(56/0.3) 4-Core PVC Insulated and FRLS Round Sheathed Multi Core Bright Annealed Bare Copper Conductor Heavy Duty Industrial Cables for Voltage Grade upto 1100 Volts as per IS: 694:1990 including all transportation charges etc complete. Makes : Finolex / RR kabel / Havells / Polycab / RPG / KEI / Nakoda / Sun cab / Sudhakar / Powerflex / Gemni / HPL / Gloster
4-Sq-mm(56/0.3) 4-core (CSSR-ELEC-2018-19)
| Basic Rate | 1 | No | 175 | 1No | 175
| Add 13.615% Contract Profit and Overhead Charges | 0.13615 | % |  |  | 23.8262
198.8262
| Deduct Tender Premium@16.01% | 0.1601 | % |  |  | 31.8321
[6 empty] | 166.9942 | 1No
55 | Supply fabrication of suitable outdoor panel with enamel coated in 16 SWG iron sheet comprising of below items internal wiring with necessary locking arrangements as mentioned below for 1 No. 20 HP open well submersible pump set of L&T/BCH of its equivalent make a) 32 Amps contactors 3 No. b) Suitable relay 1 No.c) Suitable Timer 1 No d) 100 amps MVVB of 35 KVA 1 No e)32 amps MCB for capacitor 1 No f) 0-500 Volts voltmeter Digital 1 No. g) 0-60 amps Ammeter Digital 1 No h) Capacitor 15 KV. AR 1 No. i) RYB indication lamps 1 set etc., complete as directed by the TSSC Engineers.
Electric Cable/Switch/Control Panel etc (CSSR-MRC-2018-19)
| Basic Rate | 1 | No | 56000 | 1No | 56000
| Add 5% Transport charges on Basic |  |  |  |  | 2800
58800
| Add 13.615% Contract Profit and Overhead Charges | 0.13615 | % |  |  | 8005.62
66805.62
| Deduct Tender Premium@16.01% | 0.1601 | % |  |  | 10695.5798
[6 empty] | 56110.0402 | 1No
56 | Supply, Transportation and Installation of 150mmx50mmx1.6mm thick hot dip GI perforated cable tray without cover along with coupler plates, Anchor bolts and nuts etc complete and the tray should be fitted on the wall / Ceiling etc. complete for finished item of work.
| Note: Add 30% Extra for Perforated cable tray with cover | [5 empty] | CSSR-ELEC-4.9.1.I-2018-19
| Basic Rate (CSSR-ELEC-4.9.1.I-2018-19) | 1 | Rmt | 310 | 1Rmt | 310
| Add 30% Extra |  |  |  |  | 93
403
| Add 5% Transport charges on Basic |  |  |  |  | 20.15
423.15
| Add 13.615% Contract Profit and Overhead Charges | 0.13615 | % |  |  | 57.6119
480.7619
| Deduct Tender Premium@16.01% | 0.1601 | % |  |  | 76.97
[6 empty] | 403.7919 | 1Rmt
57 | Supply and fixing air vessel made of 250 mm dia, 8 mm thick MS sheet, 1200mm in height with air release valve on top and flanged connection to riser, drain arrangement with 25mm dia Gun metal wheel valve, with required accessories, pressure gauge and painting with synthetic enamel paint of approved shade as required.
| Basic Rate (CSSR-ELEC-10.7.32-2018-19) | 1 | No | 14223 | 1No | 14223
| Add 5% Transport charges on Basic |  |  |  |  | 711.15
14934.15
| Add 13.615% Contract Profit and Overhead Charges | 0.13615 | % |  |  | 2033.2845
16967.4345
| Deduct Tender Premium@16.01% | 0.1601 | % |  |  | 2716.4863
[6 empty] | 14250.9483 | 1No
58 | Manufacture, Supply and delivery of DI D/F Gate Valves (Soft Seated) Resilient seated soft sealing gate valves (Sluice valves) with body bonnet of ductile cast iron of grade GGG-40/ SG- 400/15 or GGG-50/SG-500/7 or equivalent grade as per I.S.3896-part2-1985 and subsequent revisions, wedge fully rubber lined with EPDM food grade quality and seals of NBR and the valves should be of vacuum tight and 100% leak proof with face to face dimensions as per BS5163-89/IS14846-2000/DIN 3202 F 4. All the valves should be with Electrostatic powder coating both inside and outside pocket less body passage. Drilled as per requirement of the dept
i | A) 150MM Dia Gate Valve PN-16
| Basic Rate (as per CSSR-PH-27-2-2018-19) | 1 | No | 19577 | 1No | 19577 | (CSSR-PH-27 S o R 2-2018-19)
| Add 5% Transportation charges on Basic |  |  |  |  | 978.85
20555.85
| Add 13.615% Contract Profit and Overhead Charges |  |  |  |  | 2798.679
23354.529
| Tender Premium @16.01% |  |  |  |  | 3739.0601
[6 empty] | 19615.4689 | 1No
59 | Supply and delivery of 150mm dia CI D/F Non return valve heavy duty round body conforming IS 5312/part 1/1984, including all taxes duties etc., complete the valves shall be tested requirement ISI make labor charges etc complete as directed by the TSSC Engineers.
i | A) 150MM Dia Non Return Valve
| Basic Rate (as per CSSR-PH-26-2-2018-19) | 1 | No | 22784 | 1No | 22784 | (CSSR-PH-26 S o R 2-2018-19)
| Add 5% Transportation charges on Basic |  |  |  |  | 1139.2
23923.2
| Add 13.615% Overhead & Contract Profit |  |  |  |  | 3257.1437
27180.3437
| Tender Premium @16.01% |  |  |  |  | 4351.573
[6 empty] | 22828.7707 | 1No